## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 02.04.2018 TO 06:00 HRS OF 03.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 02.04.2018 | CCK | 43192.4118 | 43192.488 | 1:50 | LT FEEDER | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | BARA MORE SARAI-CHANDNI CHOWK. | 354
2 | 02.04.2018 | DGN | 43192.4945 | 43192.6528 | 3:48 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | REPLACEMENT OF LUGS OF 400KVA TRANSFORMER | LUGS OF 400KVA TRANSFORMER REPLACED | CHIKAMBARPUR-OLD SIMAPURI. | 42 | LUGS OF 400KVA TRANSFORMER REPLACED
3 | 02.04.2018 | JLM | 43192.5069 | 43192.6319 | 3:00 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | NEW LTAB LAID | JAGRITI ENCLAVE-ANAND VIHAR. | 129 | NEW LTAB LAID TO IMPROVE THE NETWORK
4 | 02.04.2018 | JLM | 43192.5245 | 43192.5764 | 1:15 | LT FEEDER | FIRE IN LTAB | LTAB BURNT, SAME REPAIRED | MAHARAM NAGAR-SHAHDARA. | 829
5 | 02.04.2018 | KRN | 43192.4896 | 43192.6354 | 3:30 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | TO ATTEND FAULT IN THE LINE | LT ACB FAULTY, SAME REPLACED | CHANDER NAGAR BLOCK F-GOPAL PARK. | 2329 | FAULTY LT ACB REPLACED BY NEW ONE
6 | 02.04.2018 | KRN | 43192.5271 | 43192.7177 | 4:34 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | NEW LTAB LAID | BLOCK A-BALDEV PARK EAST,KRISHNA NAGAR. | 1085 | NEW LTAB LAID TO IMPROVE THE NETWORK
7 | 02.04.2018 | KRN | 43192.5465 | 43192.6306 | 2:01 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE | WEST LAXMI MARKET KHUREJI-ARAM PARK. | 1037 | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE
8 | 02.04.2018 | KRN | 43192.5576 | 43192.6197 | 1:29 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT SOCKET BURNT, SAME REPLACED | AZAD NAGAR EAST. | 2010
9 | 02.04.2018 | KWN | 43192.6031 | 43192.6663 | 1:31 | HVDS TRANSFORMER | REPLACEMENT OF HVDS TRANSFORMER | ONE 25KVA HVDS TRANSFORMER DECLARED FAULTY, SAME REPLACED | BLOCK D-SHIV VIHAR,KARAWAL NAGAR. | 1837
10 | 03.04.2018 | KWN | 43193.2069 | 43193.2677 | 1:27 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN, SAME REPLACED | BADARPUR KHADAR,KARAWAL NAGAR. | 5071
11 | 02.04.2018 | LNR | 43192.3194 | 43192.3972 | 1:52 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY, AREA BACKFEEDED | BLOCK H-MANDAWALI VILLAGE. | 777
12 | 02.04.2018 | LNR | 43192.4653 | 43192.5284 | 1:31 | LT FEEDER | FOR TAKING LOAD ON REPAIRED CABLE | LT CABLE REPAIRED & ENERGISED | BLOCK B-VINOD NAGAR EAST. | 86
13 | 02.04.2018 | LNR | 43192.475 | 43192.6667 | 4:36 | PLANNED SHUTDOWN | MAINTENANCE WORK OF LT CIRCUIT | MAINTENANCE OF LT CIRCUIT CARRIED OUT | GURU RAMDAS NAGAR-LAKSHMI NAGAR. | 2073 | MAINTENANCE OF LT CIRCUIT CARRIED OUT
14 | 02.04.2018 | LNR | 43192.4833 | 43192.5616 | 1:53 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | REPLACEMENT OF CT | FAULTY CT REPLACED BY NEW ONE | BLOCK J-PANDAV NAGAR. | 916
15 | 02.04.2018 | LNR | 43192.4861 | 43192.566 | 1:55 | HVDS TRANSFORMER | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY, SAME REPAIRED | GANESH NAGAR EXTN.-SHAKARPUR KHAS. | 580
16 | 02.04.2018 | LNR | 43192.4965 | 43192.5438 | 1:08 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE DAMAGED DUE TO FLASH, SAME REPAIRED | BHARTI COLONY-NIRMAN VIHAR. | 88
17 | 02.04.2018 | LNR | 43192.6505 | 43192.7083 | 1:23 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | TO REPAIR LT ACB | LT ACB FAULTY, SAME REPAIRED | W-BLOCK SHAKARPUR. | 1042
18 | 03.04.2018 | MVR | 43193.0958 | 43193.1458 | 1:12 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY, AREA BACKFEEDED | GAZIPUR DAIRY FARM,GAZIPUR. | 762
19 | 02.04.2018 | NNG | 43192.5165 | 43192.5902 | 1:46 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY, SAME REPAIRED | BLOCK A-HARSH VIHAR,NAND NAGRI. | 1643
20 | 02.04.2018 | NNG | 43192.8173 | 43192.8875 | 1:41 | HVDS CABLE & OTHER SYSTEM | REPLACEMENT OF HVDS LEAD | HVDS LEAD DAMAGED DUE TO FLASH, SAME REPLACED | BLOCK E-RAJIV NAGAR,BLOCK D-MEET NAGAR. | 1125
21 | 02.04.2018 | PHG | 43192.4542 | 43192.6706 | 5:12 | PLANNED SHUTDOWN | TO ATTEND OIL LEAKAGE IN BUSHING | OIL LEAKAGE FROM LT NEUTRAL BUSHING, SAME ATTENDED | IDGAH KIOSK,MOTIA KHAN. | 980 | OIL LEAKAGE FROM LT NEUTRAL BUSHING, SAME ATTENDED
22 | 02.04.2018 | PHG | 43192.4931 | 43192.7364 | 5:50 | PLANNED SHUTDOWN | PROJECT WORK | NEW RMU INSTALLED | R.G. COMPLEX-MOTIA KHAN. | 129 | NEW RMU INSTALLED TO IMPROVE THE NETWORK
23 | 02.04.2018 | PHG | 43192.5583 | 43192.7041 | 3:30 | PLANNED SHUTDOWN | PROJECT WORK | LT CABLE END BOX MADE | CHUNA MANDI-PAHAR GANJ. | 1357 | LT CABLE END BOX MADE
24 | 02.04.2018 | PNR | 43192.5062 | 43192.6154 | 2:37 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | DISTRIBUTION BOX REPAIRED | BLOCK 24-WEST PATEL NAGAR. | 109 | FAULTY DISTRIBUTION BOX REPAIRED
25 | 02.04.2018 | PNR | 43192.5062 | 43192.6157 | 2:38 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | LT STRAIGHT THROUGH JOINT MADE | BLOCK 8-WEST PATEL NAGAR. | 20 | LT STRAIGHT THROUGH JOINT MADE
26 | 02.04.2018 | PNR | 43192.5083 | 43192.6158 | 2:35 | PLANNED SHUTDOWN | PROJECT WORK | NEW DISTRIBUTION BOX INSTALLED | BLOCK 12-WEST PATEL NAGAR. | 130 | NEW DISTRIBUTION BOX INSTALLED
27 | 02.04.2018 | PNR | 43192.5215 | 43192.5824 | 1:28 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPAIRED | INDUSTRIAL AREA-ANAND PARBHAT. | 6
28 | 02.04.2018 | PNR | 43192.5236 | 43192.616 | 2:13 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | NEW CABLE LAID | BLOCK_14B-DEV NAGAR. | 544 | NEW CABLE LAID TO INCREASE THE NETWORK CAPACITY
29 | 02.04.2018 | PNR | 43192.6028 | 43192.6821 | 1:54 | PLANNED SHUTDOWN | PROJECT WORK | LT CIRCUIT MAINTENANCE WORK CARRIED OUT | THAKKAR BAPA NAGAR-DEV NAGAR. | 316
30 | 02.04.2018 | PNR | 43192.6198 | 43192.6694 | 1:11 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRES DAMAGED DUE TO FIRE ON POLE | DAMAGED WIRE'S REPAIRED | ANAND PARBAT. | 15
31 | 02.04.2018 | SRD | 43192.4569 | 43192.5069 | 1:12 | PLANNED SHUTDOWN | PROJECT WORK | CABLE SHIFTING WORK CARRIED OUT | BLOCK_48D-NAIWALA,BLOCK_46-BEADON PURA. | 6704
32 | 02.04.2018 | SRD | 43192.4583 | 43192.5069 | 1:10 | PLANNED SHUTDOWN | PROJECT WORK | CABLE SHIFTING WORK CARRIED OUT | AJMAL KHAN PARK SRD-KAROL BAGH SRD. | 185
33 | 02.04.2018 | SRD | 43192.4583 | 43192.5729 | 2:45 | PLANNED SHUTDOWN | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | BLOCK 16-OLD RAJENDRA NAGAR. | 1710 | LOAD BALANCING CARRIED OUT TO AVOID TRIPPINGS
34 | 02.04.2018 | SRD | 43192.5972 | 43192.6678 | 1:42 | PLANNED SHUTDOWN | PROJECT WORK | LTAB MAINTENANCE WORK CARRIED OUT | BLOCK_1A-REHAGAR PURA. | 2008
35 | 03.04.2018 | VSE | 43193.1504 | 43193.1996 | 1:11 | HT SYSTEM FAULT | TO ATTEND HOT POINTS IN THE NETWORK | HOT POINTS IN THE NETWORK ATTENDED | MAYUR VIHAR PHASE III,BLOCK A & B-VASUNDHARA ENCLAVE. | 895
36 | 03.04.2018 | VSE | 43193.1625 | 43193.2444 | 1:58 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE, SAME ATTENDED | BLOCK A-MAYUR VIHAR PHASE III,BLOCK A-NEW ASHOK NAGAR. | 745
37 | 02.04.2018 | YVR | 43192.4458 | 43192.509 | 1:31 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE, SAME ATTENDED | BLOCK P-BRAHM PURI,YAMUNA VIHAR. | 4613
38 | 02.04.2018 | YVR | 43192.5444 | 43192.6365 | 2:13 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE | BLOCK P-BRAHM PURI,GAMRI-GHONDA. | 2086 | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE
39 | 02.04.2018 | YVR | 43192.5458 | 43192.6384 | 2:13 | PLANNED SHUTDOWN | PROJECT WORK | NEW CABLE LAID | BLOCK C-GHONDA PATTI. | 1379 | NEW CABLE LAID TO INCREASE THE NETWORK CAPACITY
40 | 02.04.2018 | YVR | 43192.5486 | 43192.6363 | 2:06 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | NEW CABLE LAID | BLOCK B-GARI MANDU,BLOCK B-MANUJPUR. | 2086 | NEW CABLE LAID TO INCREASE THE NETWORK CAPACITY
41 | 02.04.2018 | YVR | 43192.5493 | 43192.6719 | 2:57 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE | NON COMM AREA-SHASTRI PARK. | 1224 | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE
42 | 02.04.2018 | YVR | 43192.6007 | 43192.6538 | 1:16 | HT SYSTEM FAULT | TO INSTALL FPI | FPI INSTALLATION WORK CARRIED OUT | JAGJEET NAGAR-GHONDA,GHONDA PATTI CHAUHAN. | 6758
43 | 03.04.2018 | YVR | 43193.1722 | 43193.2722 | 2:24 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE, SAME ATTENDED,SUPPLY RESTORATION DELAYED DUE TO LOCAL SUPPLY TRF. ALSO TRIPPED IN THE GRID | ZERO PUSTA USMANPUR,SHASTRI PARK EAST. | 4491 | BIRDAGE FOUND ON LINE, SAME ATTENDED,SUPPLY RESTORATION DELAYED DUE TO LOCAL SUPPLY TRF. ALSO TRIPPED IN THE GRID