## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 03.04.2018 TO 06:00 HRS OF 04.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 03.04.2018 | CCK | 43193.876 | 43194.0265 | 3:37 | DISTRIBUTION TR. | 990KVA TRANSFORMER REPLACEMENT DUE TO OIL THEFT | TRANSFORMER REPLACED | KUCHA MOTHER KHAN, RAM BAZAAR,PART OF NIKALSON ROAD | 125 | TRANSFORMER REPLACED DUE TO OIL THEFT FROM THE SAME
2 | 03.04.2018 | DGN | 43193.45 | 43193.6376 | 4:30 | PLANNED SHUTDOWN | PROJECT WORK | LOAD BALANCING CARRIED OUT | BLOCK A-PRATAP PURA | 21 | LOAD BALANCING CARRIED OUT
3 | 03.04.2018 | DGN | 43193.4529 | 43193.5304 | 1:52 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME REPAIRED | AMBEDKAR COLONY-JHILMIL INDUSTRIAL AREA | 47
4 | 03.04.2018 | DGN | 43193.5564 | 43193.6326 | 1:50 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | BLOCK A-JHILMIL INDUSTRIAL AREA | 33
5 | 03.04.2018 | DGN | 43193.7044 | 43193.7841 | 1:55 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT LEAD FAULTY SAME REPAIRED | BLOCK-C JJ COLONY-DILSHAD COLONY | 167
6 | 03.04.2018 | JLM | 43193.5326 | 43193.7438 | 5:04 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK-C-SAVITA VIHAR | 155 | NEW LT CABLE LAID TO MEET THE LOAD
7 | 03.04.2018 | KRN | 43193.5125 | 43193.6731 | 3:51 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | RASHID MARKET-JAGATPURI | 1231 | NETWORK UPGRADTION WORK
8 | 03.04.2018 | KRN | 43193.5979 | 43193.6463 | 1:10 | PLANNED SHUTDOWN | PROJECT WORK | OLD RMU REPLACED | BLOCK F-KRISHNA NAGAR | 1302
9 | 03.04.2018 | KWN | 43193.3333 | 43193.4053 | 1:44 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME ATTENDED | POCKET -5, SONIA VIHAR | 2403
10 | 03.04.2018 | KWN | 43193.4952 | 43193.57 | 1:48 | HVDS CABLE & OTHER SYSTEM | REPLACEMENT OF HVDS TRANSFORMER | HVDS TRANSFORMER REPLACED | BHAGAT NAGAR-DAYALPUR | 1034
11 | 03.04.2018 | KWN | 43193.6345 | 43193.7118 | 1:51 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | JUMER FOUND LOOSE SAME ATTENDED | SHRI RAM COLONY KWR | 2403
12 | 03.04.2018 | KWN | 43193.6389 | 43193.7111 | 1:44 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT SOCKET BURNT SAME REPLACED | PART-6 SONIA VIHAR | 19
13 | 04.04.2018 | KWN | 43194.0028 | 43194.0789 | 1:50 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME ATTENDED | BLOCK A-KHAJURI KHAS | 256
14 | 03.04.2018 | LNR | 43193.4493 | 43193.7257 | 6:38 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK C-MADHUBAN ENCLAVE | 111 | NEW LT LEAD CONNECTED
15 | 03.04.2018 | LNR | 43193.4569 | 43193.5917 | 3:14 | LT FEEDER | DISTRIBUTION BOX FAULTY | DISTRIBUTION BOX REPLACED | BLOCK F-LALITA PARK | 575 | DISTRIBUTION BOX FAULTY SAME REPLACED
16 | 03.04.2018 | LNR | 43193.5208 | 43193.5851 | 1:33 | LT FEEDER | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | BLOCK D-VINOD NAGAR WEST | 1341
17 | 03.04.2018 | LNR | 43193.5861 | 43193.6806 | 2:16 | DISTRIBUTION TR. | OIL LEAKAGE PROBLEM FROM 990KVA TRANSFORMER | TRANSFORMER REPLACED | GADHWAALI MOHALLA LALITA PARK | 746 | OIL LEAKAGE PROBLEM FROM 990KVA TRANSFORMER SAME REPLACED
18 | 03.04.2018 | LNR | 43193.6167 | 43193.6667 | 1:12 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK F-GURU ANGAD NAGAR WEST | 85
19 | 03.04.2018 | MVR | 43193.5653 | 43193.7159 | 3:37 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK 18-KALYAN PURI | 1349 | NETWORK UPGRADTION WORK
20 | 03.04.2018 | NNG | 43193.3595 | 43193.4264 | 1:36 | LT FEEDER | TO ATTEND FAULT IN THE LINE | BIRFDAGE FOUND ON LINE SAME REMOEVD | BLOCK A-EAST GOKUL PURI | 773
21 | 03.04.2018 | NNG | 43193.4656 | 43193.5386 | 1:45 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | BLOCK D-MEET NAGAR | 170
22 | 03.04.2018 | NNG | 43193.5 | 43193.6049 | 2:31 | HT SYSTEM FAULT | FAULT IN RMU | RMU REPAIRED | POCKET- B CHITRAKOOT | 3667 | FAULT IN RMU SAME ATTENDED
23 | 03.04.2018 | NNG | 43193.5243 | 43193.5987 | 1:47 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT PANEL FLASHED SAME ATTENDED | BLOCK D-ASHOK NAGAR | 1644
24 | 03.04.2018 | NNG | 43193.5243 | 43193.5931 | 1:39 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | D-BLOCK, ASHOK NAGAR | 2550
25 | 03.04.2018 | PHG | 43193.5167 | 43193.6141 | 2:20 | PLANNED SHUTDOWN | TO REPLACE THE PIERCING CONNECTOR | PIERCING CONNECTOR REPLACED | BLOCK A-AMAR NAGAR | 881 | PIERCING CONNECTOR REPLACED
26 | 03.04.2018 | PHG | 43193.5625 | 43193.6238 | 1:28 | PLANNED SHUTDOWN | PROJECT WORK | LTAB REPLACED BY ARMOURED CABLE | BLOCK C-AMAR NAGAR | 675
27 | 03.04.2018 | PNR | 43193.4903 | 43193.5691 | 1:54 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK F-PUNJABI BASTI | 155
28 | 03.04.2018 | PNR | 43193.4938 | 43193.5693 | 1:49 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | PREM NAGAR-BALJIT NAGAR | 431
29 | 03.04.2018 | PNR | 43193.4944 | 43193.5695 | 1:48 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK 23-WEST PATEL NAGAR | 86
30 | 03.04.2018 | PNR | 43193.4951 | 43193.5699 | 1:48 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK T-FARIDPURI | 14
31 | 03.04.2018 | PNR | 43193.4951 | 43193.5698 | 1:47 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | SHADIPUR DEPOT-BALJIT NAGAR | 699
32 | 03.04.2018 | PNR | 43193.5736 | 43193.6556 | 1:58 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | REHGAR PURA PNR | 40
33 | 03.04.2018 | PNR | 43193.5736 | 43193.6583 | 2:02 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK-10B-DEV NAGAR | 78 | NETWORK UPGRADTION WORK
34 | 03.04.2018 | PNR | 43193.6 | 43193.6521 | 1:15 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME REPAIRED | BLOCK B-WEST PATEL NAGAR | 930
35 | 03.04.2018 | SRD | 43193.4634 | 43193.5326 | 1:40 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT SOCKET BURNT SAME REPLACED | GURU NANAK SUKH SABHA-NEW RAJENDRA NAGAR | 41
36 | 03.04.2018 | VSE | 43193.2514 | 43193.3275 | 1:50 | DISTRIBUTION TR. | TRANSFORMER FAULTY | TRANSFORMER REPLACED | EAST END APPARTMENT-NEW ASHOK NAGAR | 745
37 | 03.04.2018 | YVR | 43193.3778 | 43193.6819 | 7:18 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK D-BHAJANPURA | 2482 | DISTRIBUTION BOX FAULTY SAME REPLACED
38 | 03.04.2018 | YVR | 43193.3778 | 43193.6827 | 7:19 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | JAFFRABAD-MAUJ PUR | 1216 | NEW DISTRIBUTION BOX INSTALLED
39 | 03.04.2018 | YVR | 43193.3778 | 43193.6972 | 7:40 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | JANTA COLONY DWARKAPURI | 221 | NEW DISTRIBUTION BOX INSTALLED
40 | 03.04.2018 | YVR | 43193.4618 | 43193.5838 | 2:56 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK J-SILAMPUR COLONY | 184 | NEW LT LEAD CONNECTED
41 | 03.04.2018 | YVR | 43193.5007 | 43193.5591 | 1:24 | PLANNED SHUTDOWN | REPLACEMENT OF FAULTY ACB | ACB REPLACED BY NEW ONE | BLOCK B-GARI MANDU | 1230
42 | 03.04.2018 | YVR | 43193.5386 | 43193.6022 | 1:32 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | FAULT IN DISTRIBUTION BOX SAME ATTENDED | BLOCK B-NEW SILAMPURI PHASE II | 4215
43 | 03.04.2018 | YVR | 43193.5535 | 43193.6571 | 2:29 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK V-GHONDA PATTI CHAUHAN | 642 | DISTRIBUTION BOX INSTALLED
44 | 03.04.2018 | YVR | 43193.5844 | 43193.6277 | 1:02 | HT SYSTEM FAULT | REPLACEMENT OF BURNT PIERCING CONNECTOR | BURNT PIERCING CONNECTOR REPLACED | BLOCK B-MANUJPUR | 2184
45 | 03.04.2018 | YVR | 43193.6312 | 43193.6834 | 1:15 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPLACED | VILLAGE MAUJPUR | 86