## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 04.04.2018 TO 06:00 HRS OF 05.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 04.04.2018 | CCK | 43194.2896 | 43194.3611 | 1:43 | DISTRIBUTION TR. | OIL LEAKAGE FROM TRANSFORMER | OIL LEAKAGE PROBLEM ATTENDED | MAIN MARKET-KATRA DHOBI | 354
2 | 04.04.2018 | CCK | 43194.4639 | 43194.5723 | 2:36 | LT FEEDER | FIRE IN LTAB | LTAB REPAIRED | BAGH DEEWAR-CHANDNI CHOWK | 279 | FIRE IN LTAB SAME REPAIRED
3 | 04.04.2018 | CCK | 43194.6747 | 43194.7394 | 1:33 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | KASHMIRI GATE-MORI GATE | 354
4 | 04.04.2018 | DGN | 43194.4563 | 43194.5035 | 1:08 | HT SYSTEM FAULT | TRIPPING | TRANSIENT FAULT | BLOCK 1-BHAGWANPUR KHERA | 6261
5 | 04.04.2018 | DGN | 43194.4682 | 43194.5392 | 1:42 | LT FEEDER | REPAIR/REPLACEMENT OF LTAB | LTAB REPLACED | SUBHASH PARK EXTENSION | 331
6 | 04.04.2018 | DGN | 43194.474 | 43194.5398 | 1:35 | LT FEEDER | LTAB FAULTY | LTAB REPAIRED | SUBHASH PARK EXTENSION-DWARKAPURI | 121
7 | 04.04.2018 | DGN | 43194.4861 | 43194.5611 | 1:48 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | RAJIV COLONY-JHILMIL INDUSTRIAL AREA | 25
8 | 04.04.2018 | DGN | 43194.5857 | 43194.8125 | 5:27 | DISTRIBUTION TR. | 990KVA TRANSFORMER FAULTY | FAULTY TRANSFORMER REPLACED | RAM NAGAR, JAISWAL MARG DGN | 1228 | 990KVA TRANSFORMER FAULTY SAME REPLACED
9 | 04.04.2018 | KRN | 43194.4396 | 43194.5317 | 2:13 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | SUKH VIHAR-SWASTHYA VIHAR | 2754 | NETWORK UPGRADTION WORK
10 | 04.04.2018 | KRN | 43194.6157 | 43194.691 | 1:48 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | SERVICE LINE DAMAGED DUE TO FIRE ON POLE | SERVICE LINE REPAIRED | CHANDER NAGAR BLOCK D | 156
11 | 04.04.2018 | KWN | 43194.5188 | 43194.6477 | 3:06 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD BURNT SAME REPLACED | BLOCK C-MAN SINGH NAGAR | 1920 | HVDS LEAD BURNT SAME REPLACED
12 | 04.04.2018 | KWN | 43194.6091 | 43194.6903 | 1:57 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK A-TUKMIRPUR | 48
13 | 05.04.2018 | KWN | 43195.0938 | 43195.1667 | 1:45 | HT SYSTEM FAULT | CABLE END BOX DAMAGED | CABLE END BOX REPAIRED | BLOCK J-SHIV VIHAR | 5584
14 | 04.04.2018 | LNR | 43194.4688 | 43194.5174 | 1:10 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME REMOVED | BHARTI COLONY-NIRMAN VIHAR | 106
15 | 04.04.2018 | LNR | 43194.5 | 43194.5514 | 1:14 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | GURU ANGAD NAGAR EAST | 84 | CABLE FAULTY/
16 | 04.04.2018 | LNR | 43194.6181 | 43194.6713 | 1:17 | LT FEEDER | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME REMOVED | BLOCK R&A-SHAKARPUR KHAS | 1013
17 | 04.04.2018 | MVR | 43194.5209 | 43194.5912 | 1:41 | LT FEEDER | FIRE IN LTAB | LTAB REPAIRED | ACHARYA NIKETAN-SHASHI GARDEN | 79
18 | 04.04.2018 | MVR | 43194.5972 | 43194.7477 | 3:37 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK C-GAZIPUR DAIRY FARM | 248 | NETWORK UPGRADTION WORK
19 | 04.04.2018 | NNG | 43194.4783 | 43194.5582 | 1:55 | LT FEEDER | LTAB FAULTY | LTAB REPAIRED | BABARPUR EXTENSION. | 586
20 | 04.04.2018 | NNG | 43194.5213 | 43194.5972 | 1:49 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT SOCKET BURNT SAME REPLACED | BLOCK A-MANDOLI EXTENSION | 422
21 | 04.04.2018 | NNG | 43194.6312 | 43194.7117 | 1:56 | HT SYSTEM FAULT | LTAB FAULTY | LTAB REPAIRED | BLOCK D-MANDOLI EXTENSION | 412
22 | 04.04.2018 | PHG | 43194.4681 | 43194.657 | 4:32 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | ARAM NAGAR-SADAR BAZAR | 1167 | LTAB REPLACED BY ARMOURED CABLE
23 | 04.04.2018 | PHG | 43194.4886 | 43194.5379 | 1:11 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | TELI WARA-NAWAB GANJ | 675
24 | 04.04.2018 | PHG | 43194.5208 | 43194.6556 | 3:14 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | PIERCING CONNECTOR & PRC BURNT | PIERCING CONNECTOR REPLACED | BLOCK J-NABI KARIM | 670 | PIERCING CONNECTOR AND PRC BURNT SAME REPLACED
25 | 04.04.2018 | PHG | 43194.7694 | 43194.8646 | 2:17 | LT FEEDER | LT CABLE AND DISTRIBUTION BOX BURNT | LT CABLE REPLACED | GALI SANGATRASHAN BARA HINDU RAO | 392 | LT CABLE AND DISTRIBUTION BOX BURNT SAME ATTENDED
26 | 04.04.2018 | PNR | 43194.4972 | 43194.5757 | 1:53 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK 3-DEV NAGAR | 12
27 | 04.04.2018 | PNR | 43194.4979 | 43194.5759 | 1:52 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | THAKKAR BAPA NAGAR-BLOCK 16 | 544
28 | 04.04.2018 | PNR | 43194.575 | 43194.6757 | 2:25 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK T-BALJIT NAGAR | 275 | NETWORK UPGRADTION WORK
29 | 04.04.2018 | PNR | 43194.575 | 43194.6762 | 2:26 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK F-PUNJABI BASTI | 49 | NETWORK UPGRADTION WORK
30 | 04.04.2018 | PNR | 43194.575 | 43194.6761 | 2:26 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK E-PANJABI BASTI | 331 | NETWORK UPGRADTION WORK
31 | 04.04.2018 | PNR | 43194.575 | 43194.6759 | 2:25 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | DELHI MILK SCHEM DMS-PREM NAGAR | 622 | NETWORK UPGRADTION WORK
32 | 04.04.2018 | PNR | 43194.6 | 43194.6754 | 1:49 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | BAKRIWALA VILLAGE PNR | 310
33 | 04.04.2018 | SRD | 43194.3789 | 43194.4432 | 1:33 | LT FEEDER | FIRE IN LTAB | LTAB REPAIRED | KIKARWALAN SHANKAR ROAD | 1144
34 | 04.04.2018 | SRD | 43194.4285 | 43194.6186 | 4:34 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK-1A-REHAGAR PURA | 1357 | NETWORK UPGRADTION WORK
35 | 04.04.2018 | SRD | 43194.6181 | 43194.6704 | 1:15 | HT SYSTEM FAULT | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | BLOCK 20-OLD RAJENDRA NAGAR | 1042
36 | 04.04.2018 | VSE | 43194.4444 | 43194.6743 | 5:31 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK D-NEW KONDALI | 112 | NETWORK UPGRADTION WORK
37 | 04.04.2018 | VSE | 43194.4722 | 43194.6526 | 4:20 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK A-MAYUR VIHAR PHASE III | 1731 | NETWORK UPGRADTION WORK
38 | 04.04.2018 | VSE | 43194.5278 | 43194.7174 | 4:33 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK B1-NEW ASHOK NAGAR | 172 | NETWORK UPGRADTION WORK
39 | 04.04.2018 | YVR | 43194.4106 | 43194.4601 | 1:11 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | MAUJ PUR COMPLEX NO-1 | 448
40 | 04.04.2018 | YVR | 43194.447 | 43194.4952 | 1:09 | HVDS TRANSFORMER | HVDS TRANSFORMER REPLACEMENT | HVDS TRANSFORMER REPLACED | BLOCK D- LIG FLATS -NEW SILAMPURI PHASE II | 80
41 | 04.04.2018 | YVR | 43194.4714 | 43194.5282 | 1:22 | HT SYSTEM FAULT | DISTRIBUTION BOX FAULTY | DISTRIBUTION BOX BYPASSED | BLOCK C8-YAMUNA VIHAR | 1015
42 | 04.04.2018 | YVR | 43194.4931 | 43194.6774 | 4:25 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | LIG/MIG DDA FLATS-SHASTRI PARK | 1155 | NEW DISTRIBUTION BOX INSTALLED
43 | 04.04.2018 | YVR | 43194.5664 | 43194.6214 | 1:19 | HVDS TRANSFORMER | REPLACEMENT OF HVDS TRANSFORMER | HVDS TRANSFORMER REPLACED | BLOCK F- SILAMPURI PHASE-II | 162
44 | 04.04.2018 | YVR | 43194.5782 | 43194.622 | 1:03 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME REMOVED | BALI MARAN-BARA DARI | 3415
45 | 04.04.2018 | YVR | 43194.6 | 43194.6489 | 1:10 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | JUMPER FOUND LOOSE SAME ATTENDED | BLOCK E-SUBHASH MOHALLA | 2614
46 | 04.04.2018 | YVR | 43194.6861 | 43194.7303 | 1:04 | LT FEEDER | REPLACEMENT OF PIERCING CONNECTOR | PIERCING CONNECTOR REPLACED | JAFFRABAD-MAUJ PUR | 416
47 | 04.04.2018 | YVR | 43194.7687 | 43194.8131 | 1:04 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME REMOVED | JAGJEET NAGAR-GHONDA | 2663