## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 09.04.2018 TO 06:00 HRS OF 10.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 09.04.2018 | CCK | 43199.4707 | 43199.5347 | 1:32 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME REPAIRED | KATRA BARYAN-BARA DARI | 420
2 | 09.04.2018 | CCK | 43199.4951 | 43199.5611 | 1:35 | LT FEEDER | CIVIL WORK | REPLACEMENT OF FENCING AT SUBSTATION | CHAWRI BAZAR-KHUSH DIL | 177
3 | 09.04.2018 | CCK | 43199.6007 | 43199.9034 | 7:16 | LT FEEDER | LTAB BURNT DUE TO FIRE IN HOUSE | LTAB REPLACED | KUCHA MAHAJANI CCK | 774 | RESTORATION DELAYED DUE TO POLICE RESTRICTED ENTRY IN THE AREA
4 | 09.04.2018 | CCK | 43199.6007 | 43199.9026 | 7:15 | LT FEEDER | LTAB BURNT DUE TO FIRE IN HOUSE | LTAB REPLACED | KUCHA NATWA CCK | 227 | RESTORATION DELAYED DUE TO POLICE RESTRICTED ENTRY IN THE AREA
5 | 09.04.2018 | CCK | 43199.6007 | 43199.8969 | 7:06 | LT FEEDER | LTAB BURNT DUE TO FIRE IN HOUSE | LTAB REPLACED | KATRA NAWAB-CHANDNI CHOWK | 1240 | RESTORATION DELAYED DUE TO POLICE RESTRICTED ENTRY IN THE AREA
6 | 09.04.2018 | DGN | 43199.3361 | 43199.3981 | 1:29 | HT SYSTEM FAULT | TRIPPING | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK A- RESIDENTIAL FLATS DILSHAD GARDEN | 599
7 | 09.04.2018 | KRN | 43199.5278 | 43199.696 | 4:02 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK D-AJIT NAGAR | 1085 | NETWORK UPGRADTION WORK
8 | 09.04.2018 | KRN | 43199.691 | 43199.7699 | 1:54 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FIRE ON POLE | DAMAGED WIRE REPAIRED | RAGHUVIR PURA-KANTI NAGAR | 453
9 | 09.04.2018 | KWN | 43199.316 | 43199.375 | 1:25 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | C-BLOCK 3 PUSTA SONIA VIHAR | 690
10 | 09.04.2018 | KWN | 43199.3229 | 43199.4057 | 1:59 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BHAGAT NAGAR-DAYALPUR | 5147
11 | 09.04.2018 | KWN | 43199.3264 | 43199.3979 | 1:43 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK H-BHAGAT SINGH COLONY | 1041
12 | 09.04.2018 | KWN | 43199.3294 | 43199.3889 | 1:26 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE LINE SAME REMOVED | SHANTI NAGAR | 580
13 | 09.04.2018 | KWN | 43199.33 | 43199.3917 | 1:29 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | RAM MOHALLA JOHRIPUR | 425
14 | 09.04.2018 | KWN | 43199.3316 | 43199.3958 | 1:32 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | CHAMAN PARK KARAWAL NAGAR | 520
15 | 09.04.2018 | KWN | 43199.3323 | 43199.3958 | 1:31 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | SHIV VIHAR PHASE-6 | 720
16 | 09.04.2018 | KWN | 43199.3354 | 43199.3958 | 1:27 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE LINE SAME REMOVED | BLOCK C & D-INDIRA VIHAR | 5402
17 | 09.04.2018 | KWN | 43199.3375 | 43199.3847 | 1:08 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | AMAR VIHAR KARAWAL NAGAR | 345
18 | 09.04.2018 | KWN | 43199.4056 | 43199.4733 | 1:38 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | JAGDAMBA COLONY | 250
19 | 09.04.2018 | KWN | 43199.4297 | 43199.4976 | 1:38 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | SOCKET BURNT SAME REPLACED | E-BLK MAN 20 FOOTA ROAD SONIA VIHAR | 125
20 | 09.04.2018 | LNR | 43199.3389 | 43199.4132 | 1:47 | HT SYSTEM FAULT | TRIPPING | HT CABLE END TERMINATION FAULTY SAME REPAIRED | BLOCK E-LALITA PARK LNR | 2240
21 | 09.04.2018 | LNR | 43199.4132 | 43199.5764 | 3:55 | HT SYSTEM FAULT | HTAB CABLE BURNT | HTAB CABLE REPAIRED | BLOCK E-VIKAS MARG LNR | 1601 | HTAB CABLE BURNT SAME REPAIRED
22 | 09.04.2018 | LNR | 43199.4375 | 43199.6076 | 4:05 | LT FEEDER | LTAB DAMAGED DUE TO FIRE | LTAB CABLE REPAIRED | R & D BLOCK SHAKKARPUR | 1014 | LTAB DAMAGED DUE TO FIRE SAME REPAIRED
23 | 09.04.2018 | LNR | 43199.4583 | 43199.52 | 1:29 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BHARTI COLONY-NIRMAN VIHAR | 110
24 | 09.04.2018 | LNR | 43199.5436 | 43199.6007 | 1:22 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | PARK END-GAGAN VIHAR | 204
25 | 09.04.2018 | LNR | 43199.6424 | 43199.6902 | 1:09 | LT FEEDER | TO ATTEND FAULT IN THE LINE | SOCKET BURNT SAME REPLACED | BLOCK F-PREET VIHAR | 77
26 | 09.04.2018 | LNR | 43199.6556 | 43199.7091 | 1:17 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LTAB FAULTY SAME REPAIRED | BLOCK D-VINOD NAGAR WEST | 1792
27 | 09.04.2018 | LNR | 43199.8149 | 43199.8701 | 1:19 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | SERVICE LINE DAMAGED DUE TO FIRE ON POLE | DAMAGED SERVICE LINE REPAIRED | BLOCK B-GANESH NAGAR | 1348
28 | 09.04.2018 | NNG | 43199.3361 | 43199.4044 | 1:38 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | KARDAM PURI GALI NO 4,8 | 419
29 | 09.04.2018 | NNG | 43199.3375 | 43199.4135 | 1:49 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | PRIMARY SCHOOL NAND NAGRI | 510
30 | 09.04.2018 | NNG | 43199.3452 | 43199.42 | 1:48 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | D-BLOCK HARSH VIHAR | 421
31 | 09.04.2018 | NNG | 43199.3456 | 43199.4208 | 1:48 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK D-MEET NAGAR | 1126
32 | 09.04.2018 | NNG | 43199.3474 | 43199.4223 | 1:48 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK B-SEWA DHAM | 124
33 | 09.04.2018 | NNG | 43199.3479 | 43199.4225 | 1:48 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | SOCKET BURNT SAME REPLACED | CHUNA BHATTI MANDOLI | 410
34 | 09.04.2018 | NNG | 43199.4924 | 43199.5583 | 1:35 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK L-SUNDER NAGRI | 1055
35 | 09.04.2018 | PHG | 43199.4986 | 43199.6851 | 4:29 | LT FEEDER | PIERCING CONNECTOR BURNT | PIERCING CONNECTOR REPLACED | ARAM NAGAR-SADAR BAZAR | 119 | PIERCING CONNECTOR BURNT SAME REPLACED
36 | 09.04.2018 | PNR | 43199.5049 | 43199.5956 | 2:11 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK 22-WEST PATEL NAGAR | 22 | NETWORK UPGRADTION WORK
37 | 09.04.2018 | PNR | 43199.5049 | 43199.5955 | 2:10 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK 8-WEST PATEL NAGAR | 20 | NETWORK UPGRADTION WORK
38 | 09.04.2018 | PNR | 43199.5056 | 43199.5986 | 2:14 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK E-WEST PATEL NAGAR | 130 | NETWORK UPGRADTION WORK
39 | 09.04.2018 | PNR | 43199.5056 | 43199.5958 | 2:10 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK 23-WEST PATEL NAGAR | 86 | NETWORK UPGRADTION WORK
40 | 09.04.2018 | PNR | 43199.516 | 43199.5698 | 1:18 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | ARMY QUARTER'S-ANAND PARBAT | 14
41 | 09.04.2018 | PNR | 43199.5389 | 43199.619 | 1:55 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK-14B-DEV NAGAR | 544
42 | 09.04.2018 | PNR | 43199.5389 | 43199.6192 | 1:56 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | MATA RAMESHWARI NEHRU NAGAR-DEV NAGAR | 207
43 | 09.04.2018 | SRD | 43199.4618 | 43199.5133 | 1:14 | HT SYSTEM FAULT | FOR ATTENDING HOT SPOT | HOT SPOT ATTENDED | BLOCK-47-BEADON PURA | 1046
44 | 09.04.2018 | SRD | 43199.4796 | 43199.5371 | 1:23 | HT SYSTEM FAULT | TREE BRANCHES TOUCHING THE LINE | TREE TRIMMING CARRIED OUT | BLOCK-45-KRISHNA NAGAR | 1100
45 | 09.04.2018 | VSE | 43199.5083 | 43199.6804 | 4:08 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | PKT 3-NEW KONDALI | 69 | NETWORK UPGRADTION WORK
46 | 09.04.2018 | YVR | 43199.3611 | 43199.4187 | 1:23 | HT SYSTEM FAULT | TRIPPING | HVDS TRANSFORMER FUSE BLOWN SAME REPLACED | BLOCK A-SHASTRI PARK | 105
47 | 09.04.2018 | YVR | 43199.3826 | 43199.4639 | 1:57 | HT SYSTEM FAULT | TRIPPING | ELECTROCUTION OF EXTERNAL ELEMENTS | BLOCK B-MANUJPUR | 6037
48 | 09.04.2018 | YVR | 43199.4819 | 43199.5628 | 1:56 | PLANNED SHUTDOWN | REPLACEMENT OF FAULTY DISTRIBUTION BOX | DISTRIBUTION BOX REPLACED | VILLAGE-MAUJ PUR | 259
49 | 09.04.2018 | YVR | 43199.4885 | 43199.5606 | 1:44 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | ELECTROCUTION OF EXTERNAL ELEMENTS | GHONDA PATTI CHAUHAN | 521
50 | 09.04.2018 | YVR | 43199.5153 | 43199.6203 | 2:31 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | CHAUHAN BANGAR-JAFFRABAD | 3786 | NETWORK UPGRADTION WORK
51 | 09.04.2018 | YVR | 43199.5236 | 43199.7186 | 4:41 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | LIG/MIG FLATS-SHASTRI PARK | 1155 | NETWORK UPGRADTION WORK
52 | 09.04.2018 | YVR | 43199.5438 | 43199.614 | 1:41 | HT SYSTEM FAULT | FOR CONNECTING REPAIRED CABLE | REPAIRED CABLE CONNECTED | JAFFRABAD VILLAGE | 1245
53 | 09.04.2018 | YVR | 43199.5514 | 43199.6084 | 1:22 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | DP FUSE BLOWN SAME REPLACED | MAUJ PUR COMPLEX 1 | 2198
54 | 09.04.2018 | YVR | 43199.6007 | 43199.7243 | 2:58 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | NEW USMANPUR-NEW KATWARA | 1230 | NETWORK UPGRADTION WORK
55 | 09.04.2018 | YVR | 43199.6375 | 43199.7246 | 2:05 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | SUBHASH PARK-GORAKH PARK,JAFFRABAD-MAUJ PUR, | 857 | NETWORK UPGRADTION WORK
56 | 09.04.2018 | YVR | 43199.8278 | 43199.8975 | 1:40 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE LINE SAME REMOVED | BLOCK B-GARI MANDU | 1025