## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 12.04.2018 TO 06:00 HRS OF 13.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 12.04.2018 | CCK | 43202.2521 | 43202.334 | 1:58 | HT SYSTEM FAULT | TRIPPING | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | GALI CHOODI WAALI CCK | 491
2 | 12.04.2018 | CCK | 43202.2972 | 43202.3622 | 1:34 | HT SYSTEM FAULT | TRIPPING | HT PANEL FLASHED SAME REPAIRED | GALI QASHIM JAAN CCK | 2977
3 | 12.04.2018 | CCK | 43202.2972 | 43202.3657 | 1:39 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT PANEL FLASHED SAME ATTENDED | NIGAM BODH GHAAT | 1228
4 | 12.04.2018 | CCK | 43202.3523 | 43202.4296 | 1:51 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT LEAD FAULTY SAME REPAIRED | MORI GATE CCK | 65
5 | 12.04.2018 | CCK | 43202.4951 | 43202.5591 | 1:32 | LT FEEDER | TO ATTEND FAULT IN THE LINE | DP FUSE BLOWN SAME REPLACED | GHEE MANDI CCK | 574
6 | 12.04.2018 | CCK | 43202.5199 | 43202.584 | 1:32 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | NEW HAUZ QUAZI CCK | 388
7 | 12.04.2018 | DGN | 43202.2903 | 43202.3403 | 1:12 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | C BLOCK LONI ROAD | 6277
8 | 12.04.2018 | DGN | 43202.5571 | 43202.6125 | 1:20 | HT SYSTEM FAULT | TRIPPING | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | NEW DUJANA HOUSE | 1455
9 | 12.04.2018 | DGN | 43202.5571 | 43202.708 | 3:37 | HT SYSTEM FAULT | LT ACB FLASHED | LT ACB REPLACED | FRIENDS COLONY DGN | 164 | LT ACB FLASHED SAME REPLACED
10 | 12.04.2018 | DGN | 43202.5571 | 43202.6785 | 2:55 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME REPAIRED | F BLOCK DILSHAD GARDEN | 164 | LT LEAD FAULTY SAME REPAIRED
11 | 12.04.2018 | DRG | 43202.4413 | 43202.4925 | 1:14 | DISTRIBUTION TR. | OIL LEAKAGE FROM TRANSFORMER | OIL LEAKAGE PROBLEM ATTENDED | GIRDHAR PANNA DRG | 52
12 | 12.04.2018 | DRG | 43202.5417 | 43202.5952 | 1:17 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | SHEESH MAHAL DRG | 1775
13 | 12.04.2018 | DRG | 43202.5417 | 43202.5969 | 1:19 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | COMMUNITY CENTRE-JAMA MASZID | 298
14 | 12.04.2018 | DRG | 43202.6131 | 43202.68 | 1:36 | PLANNED SHUTDOWN | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | PATOUDI HOUSE DRG | 592
15 | 12.04.2018 | JLM | 43202.5139 | 43202.6667 | 3:40 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | C BLOCK JHILMILL COLONY | 22 | NEW LTAB LAID TO IMPROVE THE NETWORK
16 | 12.04.2018 | KRN | 43202.5278 | 43202.597 | 1:40 | LT FEEDER | FOR CONNECTING REPAIRED CABLE | REPAIRED CABLE CONNECTED | E-BLOCK KRISHNA NAGAR | 1216
17 | 12.04.2018 | KRN | 43202.5292 | 43202.6935 | 3:57 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK 9-DHARAM PURA | 1464 | NETWORK UPGRADATION WORK
18 | 12.04.2018 | KRN | 43202.566 | 43202.6388 | 1:45 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | SERVICE LINE DAMAGED DUE TO FIRE ON POLE | SERVICE LINE REPAIRED | WELCOME COLONY SEELAMPUR | 453
19 | 12.04.2018 | KRN | 43202.5799 | 43202.652 | 1:44 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | SERVICE LINE DAMAGED DUE TO FIRE ON POLE | SERVICE LINE REPAIRED | CHANDER NAGAR | 752
20 | 12.04.2018 | KRN | 43202.6771 | 43202.7428 | 1:35 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT LAED FAULTY SAME ATTENDED | 12-BLOCK GEETA COLONY | 752
21 | 12.04.2018 | KWN | 43202.2661 | 43202.3313 | 1:34 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | GALI NO2 ANKUR ENCLAVE | 173
22 | 12.04.2018 | KWN | 43202.3542 | 43202.4236 | 1:40 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BADARPUR KHADAR | 911
23 | 12.04.2018 | KWN | 43202.3791 | 43202.4512 | 1:44 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | PHASE-6 SHIV VIHAR | 1826
24 | 12.04.2018 | KWN | 43202.4847 | 43202.5522 | 1:37 | LT FEEDER | LTAB CONDUCTOR DAMAGED | LTAB CONDUCTOR REPAIRED | JOHRIPUR VILLAGE | 1361
25 | 12.04.2018 | KWN | 43202.5236 | 43202.6025 | 1:54 | HVDS TRANSFORMER | REPLACEMENT OF HVDS TRANSFORMER | HVDS TRANSFORMER REPLACED | AMAR VIHAR, PANCHAL VIHAR | 130
26 | 12.04.2018 | KWN | 43202.5243 | 43202.6929 | 4:03 | PLANNED SHUTDOWN | FOR REPLACING DAMAGED HVDS LEAD | HVDS LEAD REPLACED | BLOCK C-MAN SINGH NAGAR | 1920 | FOR REPLACING DAMAGED HVDS LEAD
27 | 12.04.2018 | KWN | 43202.6609 | 43202.7319 | 1:42 | PLANNED SHUTDOWN | FAULT IN HT O/H CIRCUIT | TREE TRIMMING | 4.5-PUSTA SERVICE ROAD SONIA VIHAR | 302
28 | 12.04.2018 | KWN | 43202.8556 | 43202.9285 | 1:45 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | DEVI NAGAR KWR | 2391
29 | 12.04.2018 | LNR | 43202.4444 | 43202.708 | 6:20 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK D-PREET VIHAR | 55 | NETWORK UPGRADTION WORK
30 | 12.04.2018 | LNR | 43202.4514 | 43202.5354 | 2:01 | DISTRIBUTION TR. | TRANSFORMER SHIFTING | TRANSFORMER SHIFTED | VILLAGE MANDAWALI | 86 | TRANSFORMER SHIFTING WORK
31 | 12.04.2018 | LNR | 43202.4644 | 43202.5444 | 1:55 | LT FEEDER | REPLACEMENT OF LT AB | LTAB CONDUCTOR REPLACED | BLOCK-5 GURU ANGAD NAGAR | 41
32 | 12.04.2018 | LNR | 43202.5 | 43202.5708 | 1:42 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | D BLOCK SHAKKARPUR | 1479
33 | 12.04.2018 | LNR | 43202.5872 | 43202.6454 | 1:24 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT SOCKET BURNT SAME REPLACED | DVB STAFF QUARTE'S LNR | 562
34 | 12.04.2018 | LNR | 43202.6487 | 43202.7049 | 1:21 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT SOCKET BURNT SAME REPLACED | LALIT PARK LNR | 1445
35 | 12.04.2018 | MVR | 43202.4939 | 43202.616 | 2:56 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT POLE DAMAGED BY UNKNOWN VEHICLE | DAMAGED POLE REPLACED | MUNNI BORDER MVR | 1843 | LT POLE DAMAGED BY UNKNOWN VEHICLE SAME REPLACED
36 | 12.04.2018 | MVR | 43202.6179 | 43202.6947 | 1:50 | LT FEEDER | TO ATTEND FAULT IN THE LINE | CURRENT LEAKAGE PROBLEM FROM THE POLE SAME ATTENDED | B-BLOCK MAYUR VIHAR PHASE-2 | 264
37 | 12.04.2018 | NNG | 43202.288 | 43202.3512 | 1:31 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | MEET NAGAR KWR | 1491
38 | 12.04.2018 | NNG | 43202.3622 | 43202.4267 | 1:33 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | C BLOCK MEET NAGAR | 235
39 | 12.04.2018 | NNG | 43202.5282 | 43202.599 | 1:42 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LTAB FAULTY SAME REPAIRED | GAGAN CINEMA STREET | 261
40 | 12.04.2018 | NNG | 43202.7117 | 43202.778 | 1:35 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | C-BLOCK HARSH VIHAR | 1126
41 | 12.04.2018 | NNG | 43202.9847 | 43203.0444 | 1:26 | PLANNED SHUTDOWN | HVDS CIRCUIT | REPAIR/REPLACEMENT WORK OF HVDS CABLE | MAHAVEER GALI VIA MANDOLI | 432
42 | 12.04.2018 | VSE | 43202.6243 | 43202.6966 | 1:44 | PLANNED SHUTDOWN | REPLACEMENT OF DAMAGED LTAB | DAMAGED LTAB REPLACED | BLOCK C1-NEW ASHOK NAGAR | 1142
43 | 12.04.2018 | YVR | 43202.4354 | 43202.6052 | 4:05 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK C-GHONDA | 642 | NEW DISTRIBUTION BOX INSTALLED
44 | 12.04.2018 | YVR | 43202.4354 | 43202.5907 | 3:44 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BHAGAT NAGAR-DAYALPUR | 1566 | NETWORK UPGRADTION WORK
45 | 12.04.2018 | YVR | 43202.4528 | 43202.59 | 3:18 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | GHONDA PATTI CHAUHAN | 86 | NEW DISTRIBUTION BOX INSTALLED
46 | 12.04.2018 | YVR | 43202.4541 | 43202.5175 | 1:31 | HT SYSTEM FAULT | FOR REMOVING ILLEGAL TAPPING | ILLEGAL TAPPING REMOVED | DDA COMPLEX SHASTRI PARK | 1055
47 | 12.04.2018 | YVR | 43202.4661 | 43202.5845 | 2:50 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT LEAD FAULTY SAME REPAIRED | C-7, YAMUNA VIHAR | 906 | HT LEAD FAULTY SAME REPAIRED
48 | 12.04.2018 | YVR | 43202.4764 | 43202.5924 | 2:47 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK P-BRAHM PURI | 1676 | NETWORK UPGRADTION WORK
49 | 12.04.2018 | YVR | 43202.4861 | 43202.5375 | 1:14 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME REMOVED | VIJAY PARK YVR | 2014
50 | 12.04.2018 | YVR | 43202.4869 | 43202.5675 | 1:56 | HT SYSTEM FAULT | FOR ATTENDING HOT SPOT | HOT SPOT ATTENDED | D-BLK. GAMARI EXTENSION | 10324
51 | 12.04.2018 | YVR | 43202.6097 | 43202.7074 | 2:21 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | ZERO PUSTA-USMAN PUR | 154 | NEW DISTRIBUTION BOX INSTALLED
52 | 12.04.2018 | YVR | 43202.6569 | 43202.7216 | 1:33 | HT SYSTEM FAULT | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | YAMUNA FLOOD PLAINS YVR | 3961
53 | 12.04.2018 | YVR | 43202.6615 | 43202.7078 | 1:07 | HT SYSTEM FAULT | FIRE IN DISTRIBUTION BOX | DISTRIBUTION BOX BYPASSED | SOUTH WAZIRABAD | 1379
54 | 12.04.2018 | YVR | 43202.8243 | 43202.9145 | 2:10 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT ACB FLASHED SAME REPAIRED | CHAUHAN BANGAR GALI NO-10 | 3733 | LT ACB FLASHED SAME REPAIRED