## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 13.04.2018 TO 06:00 HRS OF 14.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 13.04.2018 | DGN | 43203.6696 | 43203.7414 | 1:43 | LT FEEDER | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | ICE FACTORY DWARKAPURI | 204
2 | 13.04.2018 | DGN | 43203.7203 | 43203.7688 | 1:10 | HT SYSTEM FAULT | TRIPPING | SOCKET DAMAGE SAME REPAIRED | B-BLOCK JHILMIL | 2082
3 | 13.04.2018 | DRG | 43203.4653 | 43203.5773 | 2:41 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | CHANDANI MAHAL | 298 | NETWORK UPGRADTION WORK
4 | 13.04.2018 | JLM | 43203.4847 | 43203.5486 | 1:32 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK C-VIGYAN VIHAR, | 181
5 | 13.04.2018 | KRN | 43203.4417 | 43203.5017 | 1:26 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | SOCKET FAULTY SAME REPAIRED | CHANDAR NAGAR | 2124
6 | 13.04.2018 | KRN | 43203.4479 | 43203.61 | 3:53 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | DHRAM PURA-KAILASH NAGAR | 942 | NETWORK UPGRADTION WORK
7 | 13.04.2018 | KRN | 43203.6724 | 43203.7535 | 1:57 | LT FEEDER | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | SUBHASH MOHALLA | 60
8 | 13.04.2018 | KWN | 43203.4688 | 43203.5139 | 1:05 | LT FEEDER | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | SHADATPUR | 1186
9 | 13.04.2018 | KWN | 43203.5241 | 43203.5799 | 1:20 | HVDS TRANSFORMER | HVDS TRANSFORMER FAULTY | REPLACEMENT WORK OF HVDS TRANSFORMER | A-BLOCK AMAR VIHAR | 268
10 | 13.04.2018 | KWN | 43203.5778 | 43203.6597 | 1:58 | HVDS CABLE & OTHER SYSTEM | HVDS CIRCUIT | REPAIR/REPLACEMENT WORK OF HVDS CABLE | SHANTI NAGAR | 312
11 | 13.04.2018 | KWN | 43203.5979 | 43203.7444 | 3:31 | LT FEEDER | FAULT IN LT CIRCUIT | LTAB FAULTY SAME REPAIRED | SOME PART OF KARAWAL NAGAR VILLAGE | 280 | LTAB FAULTY SAME REPAIRED
12 | 13.04.2018 | KWN | 43203.6042 | 43203.684 | 1:55 | HVDS CABLE & OTHER SYSTEM | HVDS CIRCUIT | REPAIR/REPLACEMENT WORK OF HVDS CABLE | SHIV VIHAR | 412
13 | 13.04.2018 | KWN | 43203.7153 | 43203.7778 | 1:30 | HVDS CABLE & OTHER SYSTEM | HVDS CIRCUIT | HVDS CABLE FAULTY SAME REPAIRED | POLICE STN BHAJURI | 3431
14 | 13.04.2018 | KWN | 43203.7581 | 43203.809 | 1:13 | HVDS CABLE & OTHER SYSTEM | HVDS CIRCUIT | REPAIR/REPLACEMENT WORK OF HVDS CABLE | B-BLOCK AMAR VIHAR | 2901
15 | 13.04.2018 | KWN | 43203.7951 | 43203.9403 | 3:29 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | PREM VIHAR KARAWAL NAGAR | 280 | HVDS DP FUSE BLOWN SAME REPLACED
16 | 13.04.2018 | KWN | 43203.816 | 43203.875 | 1:25 | HVDS CABLE & OTHER SYSTEM | HVDS CABLE FAULTY | HVDS CABLE FAULTY SAME REPAIRED | D-BLOCK AMAR VIHAR | 340
17 | 13.04.2018 | KWN | 43203.8465 | 43203.9819 | 3:15 | HT SYSTEM FAULT | HVDS CABLE FAULTY | HVDS CABLE FAULTY SAME REPAIRED | C-BLOCK WEST KARAWAL NAGAR | 1567 | HVDS CABLE FAULTY SAME REPAIRED
18 | 13.04.2018 | KWN | 43203.8806 | 43203.9361 | 1:20 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | JAGDAMBA COLONY | 6932
19 | 13.04.2018 | KWN | 43203.9042 | 43204.1952 | 6:59 | HVDS CABLE & OTHER SYSTEM | HVDS CABLE FAULTY | HVDS CABLE FAULTY SAME REPAIRED | SHIV VIHAR PHASE-6 | 320 | HVDS CABLE FAULTY SAME REPAIRED
20 | 14.04.2018 | KWN | 43204.1944 | 43204.2833 | 2:08 | HT SYSTEM FAULT | HVDS CABLE FAULTY | HVDS CABLE FAULTY SAME REPAIRED | BADARPUR KHADAR, VILLAGE SABHAPUR | 408 | HVDS CABLE FAULTY SAME REPAIRED
21 | 14.04.2018 | KWN | 43204.2033 | 43204.2569 | 1:17 | HT SYSTEM FAULT | HVDS CABLE FAULTY | HVDS CABLE FAULTY SAME REPAIRED | DEVI NAGAR KARAWAL NAGAR | 302 | HVDS CABLE FAULTY SAME REPAIRED
22 | 14.04.2018 | KWN | 43204.2153 | 43204.2972 | 1:58 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | C-1 SONIA VIHAR | 348 | HVDS DP FUSE BLOWN SAME REPLACED
23 | 14.04.2018 | KWN | 43204.25 | 43204.3063 | 1:21 | HT SYSTEM FAULT | HVDS CABLE FAULTY | HVDS CABLE FAULTY SAME REPAIRED | B-BLOCK SONIA VIHAR | 290 | HVDS CABLE FAULTY SAME REPAIRED
24 | 13.04.2018 | LNR | 43203.484 | 43203.5653 | 1:57 | LT FEEDER | LOAD SHIFTING WORK | FOR TAKING LOAD ON REPAIRED CABLE | MANDAWALI | 664
25 | 13.04.2018 | LNR | 43203.5028 | 43203.5531 | 1:12 | HT SYSTEM FAULT | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | B-BLOCK PREET VIHAR | 53
26 | 13.04.2018 | LNR | 43203.5167 | 43203.7438 | 5:27 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK G-PREET VIHAR, | 164 | NETWORK UPGRADTION WORK
27 | 13.04.2018 | LNR | 43203.5863 | 43203.6632 | 1:51 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT | MOBILE TRANSFORMER REPLACEMENT | LAXMI NAGAR | 855
28 | 13.04.2018 | MVR | 43203.4757 | 43203.6621 | 4:28 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | MAYUR VIHAR,ACHARYA NIKETAN-SHASHI GARDEN, | 1715 | NETWORK UPGRADTION WORK
29 | 13.04.2018 | NNG | 43203.338 | 43203.4141 | 1:50 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME REPAIRED | D-BLOCK MEET NAGAR | 456
30 | 13.04.2018 | NNG | 43203.3392 | 43203.4162 | 1:51 | LT FEEDER | LTAB CONDUCTOR DAMAGED | LTAB CONDUCTOR REPAIRED | B-BLOCK MEET NAGAR | 549
31 | 13.04.2018 | NNG | 43203.4369 | 43203.5134 | 1:50 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LTAB FAULTY SAME REPAIRED | C-BLOCK GOKULPURI | 278
32 | 13.04.2018 | NNG | 43203.4816 | 43203.5581 | 1:50 | LT FEEDER | LOAD REDUCED | FIRE ON POLE SAME ATTENDED | MANSAROVAR PARK | 315
33 | 13.04.2018 | NNG | 43203.5519 | 43203.6132 | 1:28 | HT SYSTEM FAULT | HVDS CIRCUIT | HVDS DP FUSE BLOWN SAME REPLACED | VISHNU GALI NAND NAGRI | 255
34 | 13.04.2018 | NNG | 43203.5527 | 43203.6043 | 1:14 | HT SYSTEM FAULT | HVDS CIRCUIT | BIRDAGE FOUND ON LINE SAME REMOVED | DJB STP YAMUNA VIHAR | 245
35 | 13.04.2018 | NNG | 43203.6177 | 43203.6654 | 1:09 | LT FEEDER | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | JANTA COLONY YAMUNA VIHAR | 739
36 | 13.04.2018 | NNG | 43203.6603 | 43203.7119 | 1:14 | HVDS CABLE & OTHER SYSTEM | HVDS CABLE FAULTY | HVDS CABLE FAULTY SAME REPAIRED | NAND NAGRI | 124
37 | 13.04.2018 | NNG | 43203.756 | 43203.8012 | 1:05 | HT SYSTEM FAULT | CABLE END BOX DAMAGED | CABLE END BOX DAMAGED SAME REPAIRED | C-BLOCK HARSH BIHAR | 125
38 | 13.04.2018 | PHG | 43203.5097 | 43203.6963 | 4:29 | PLANNED SHUTDOWN | FAULT IN LT CIRCUIT | TO REPLACE THE PIERCING CONNECTOR | CHUNA MANDI-PAHAR GANJ | 65 | TO REPLACE THE PIERCING CONNECTOR
39 | 13.04.2018 | PNR | 43203.4826 | 43203.5722 | 2:09 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK F-PUNJABI BASTI | 6 | NETWORK UPGRADTION WORK
40 | 13.04.2018 | PNR | 43203.4826 | 43203.5726 | 2:10 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK 35-RAMJAS SPORTS COMPLEX,CLOSED FACTORY-FARIDPURI | 14 | NETWORK UPGRADTION WORK
41 | 13.04.2018 | PNR | 43203.4826 | 43203.5723 | 2:09 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK T-BALJIT NAGAR, SHADIPUR DEPOT- BALJIT NAGAR | 699 | NETWORK UPGRADATION WORK
42 | 13.04.2018 | PNR | 43203.4826 | 43203.5725 | 2:09 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | BLOCK F-PUNJABI BASTI,PREM NAGAR | 431 | NETWORK UPGRADATION WORK
43 | 13.04.2018 | PNR | 43203.4972 | 43203.5654 | 1:38 | HT SYSTEM FAULT | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | S-BLOCK WEST PATEL NAGAR | 330
44 | 13.04.2018 | PNR | 43203.5056 | 43203.5556 | 1:12 | DISTRIBUTION TR. | OIL LEAKAGE FROM TRANSFORMER | OIL LEAKAGE PROBLEM ATTENDED | H.S. ROAD PRASAD NAGAR | 2352
45 | 13.04.2018 | PNR | 43203.5823 | 43203.6556 | 1:46 | LT FEEDER | FAULT IN LT CIRCUIT | REPAIR OF DAMAGED WIRE ON POLES | B-BLOCK WEST PATEL NAGAR | 192
46 | 13.04.2018 | PNR | 43203.6931 | 43203.7639 | 1:42 | HT SYSTEM FAULT | TRIPPING | CABLE BURNT SAME REPAIRED | TAULIWALAN ANAND PARVAT | 2081
47 | 13.04.2018 | PNR | 43203.7639 | 43203.8778 | 2:44 | LT FEEDER | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | PART OF NEHRU NAGAR PATEL NAGAR | 1022 | LEAD FAULTY SAME REPAIRED
48 | 13.04.2018 | VSE | 43203.5257 | 43203.6935 | 4:02 | PLANNED SHUTDOWN | FAULT IN LT CIRCUIT | REPLACEMENT WORK OF THE SERVICE LINE | BLOCK B1-NEW ASHOK NAGAR | 827 | REPLACEMENT WORK OF THE SERVICE LINE
49 | 13.04.2018 | VSE | 43203.7615 | 43203.8221 | 1:27 | LT FEEDER | FAULT IN LT CIRCUIT | JUMPER DAMAGED SAME REPLACED | NEW ASHOK NAGAR | 1813
50 | 13.04.2018 | YVR | 43203.4257 | 43203.621 | 4:41 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK C-BHAJANPURA | 1545 | NETWORK UPGRADATION WORK
51 | 13.04.2018 | YVR | 43203.4312 | 43203.4923 | 1:28 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT SOCKET BURNT SAME REPLACED | ZERO PUSTA USHMANPUR | 223
52 | 13.04.2018 | YVR | 43203.4396 | 43203.5192 | 1:55 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT LEAD FAULTY SAME REPAIRED | B-BLOCK YAMUNA VIHAR | 548
53 | 13.04.2018 | YVR | 43203.466 | 43203.59 | 2:59 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | JAFFRABAD-MAUJ PUR | 448 | NETWORK UPGRADTION WORK
54 | 13.04.2018 | YVR | 43203.4756 | 43203.5246 | 1:11 | HT SYSTEM FAULT | RMU MAINTENANCE | REPAIR/REPLACEMENT OF DEFECTIVE MECHANISM | BHAJANPURA | 4213
55 | 13.04.2018 | YVR | 43203.6146 | 43203.7205 | 2:33 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADTION WORK | SUBHASH PARK-GORAKH PARK, | 314 | NETWORK UPGRADTION WORK