## Format
DISCOM : BRPL
OUTAGE REPORT FOR : 15/04/2018 06:00Hr. To 16/04/2018 06:00Hr.
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Area / DT Effected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Detail
1 | 15/04/2018 | DWK | 06:36 | 08:00 | 01:23 | HT SYSTEM FAULT | Grid:G-15 DWARKA REL. ENERGY GRID SSTN To Feeder:11kV FDR KARGIL CHOWK , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : 630 TRF-1:SEC-11 SSTN-4*,*S/STN 1, 63 PLOTS SECT.11 DWK*,*630 TRF-2:,SEC-11 I/D PKT-4 S/S-3* | 378
2 | 15/04/2018 | MDK | 07:26 | 08:28 | 01:02 | HT SYSTEM FAULT | Grid:NANGLOI WATER WORKS (66/11kV) GRID SSTN To Feeder:11kV FDR TIKRI FDR , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : 400TRF-1: GALI NO 2 IND AREA MUNDKA(SOUTH) 8*,*100TRF-1:SSTN -19 SOUTH GALI-1 MDK P/M*,*100TRF-1:TRF NO 13 GALI NO 2 IND AREA MUNDKA*,*100TRF-1:SSTN -3 SOUTH GALI-1 MDK P/M*,*100TRF-1:SSTN -7 SOUTH GALI-1 MDK P/M*,*100TRF-1:OMNI PLASTIC*,*100TRF-1:SSTN -5 SOUTH GALI-1 MDK P/M*,*400TRF-1:SSNO 8 NEAR MTNL TOWER*,*100TRF-1:MTNL TOWER FIRNI ROAD MUNDKA*,*100TRF-1:PLOT NO. 28 GALI NO.2 MUNDKA*,*100TRF-1:SSTN -2 SOUTH GALI-1 MDK*,*100TRF-1:TRF NO 10 GALI NO 2 IND AREA*,*100TRF-1:PLOT NO.93/16and93/17 MUNDKA*,*100TRF-1:84/25/1 VIL MDK KULDEP VINOD K*,*100TRF-1:TRF NO 15 GALI NO 2 IND AREA*,*100TRF-1:B/P ROHTAK ROAD MUNDKA:PM*,*100TRF-1:SSTN -6 SOUTH GALI-1 MDK P/M*,*100TRF-1:SAMTEC CO. AT KHASRA NO. 92/6/1 | 471
3 | 15/04/2018 | PJB | 08:40 | 10:04 | 01:23 | HT SYSTEM FAULT | Grid:PASCHIM PURI (33/11kV) GRID SSTN To Feeder:A-2 COMMUNITY CENTER , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : 630 TRF-1: A-3 BLK NR CA APPT.,PASCHIM VHR*,*630 TRF-2: CA APPT.-1,PASCHIM VHR*,*PASCHIM VHR*,*400 TRF-2: A-2 LIG FLATS,PASCHIM VHR,PJB*,*400 TRF-2: A-2 COMMUNITY CNTR,PASCHIM VHR*,*400 TRF-1: CA APPT.-1,PASCHIM VHR*,*630 TRF-1: A-2 LIG FLATS,PASCHIM VHR,PJB | 547
4 | 15/04/2018 | KPR | 09:19 | 10:45 | 01:25 | HVDS CABLE & OTHER SYSTEM | Grid:66kV BATRA GRID To Feeder:11kV FDR L-15 SANGAM VIHAR , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : TRF-1 HARIZAN BASTI:PL | 245
5 | 15/04/2018 | NGL | 10:00 | 13:24 | 03:24 | PLANNED SHUTDOWN | Grid:UDYOG NAGAR (33/11kV) GRID SSTN To Feeder:11kV FDR SSTN-5 VIA K-25 , TRANSFORMER:TO REPLACE OIL SEAL | RESTORED/ REPAIRED | Part of : 990 TRF-2: I/D UDYOG NAGAR S/STN-5*,*630 TRF-3:UDYOG NAHAR SSTN-5 | 469
6 | 15/04/2018 | VKP | 10:02 | 11:31 | 01:29 | LT FEEDER | Grid:BODELLA-II GRID To Feeder:11KV HASTAL SOCIETY NO.-1 , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : *630 TRF-1:RAJDHANI PUBLIC SCHOOL:PL* | 78
7 | 15/04/2018 | KPR | 10:05 | 11:26 | 01:20 | EMERGENCY SHUTDOWN | Grid:66 kV OKHLA PHASE-I GRID To Feeder:11kV FDR I-BLOCK, LAL KUAN , TRANSFORMER:REPLACEMENT OF CABLE | RESTORED/ REPAIRED | Part of : *TRF-1 CHUNGI NO.3:PL* | 137
8 | 15/04/2018 | SVR | 10:21 | 11:43 | 01:21 | LT FEEDER | Grid:66/11KV MEETHAPUR GRID SUB STN To Feeder:11kV FDR OM NAGAR GALI NO-10 A B &C BLOCK , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : *TRF-1 GALI NO.-2 B-BLK. SHAKTI VIHAR | 194
9 | 15/04/2018 | SKT | 11:00 | 13:54 | 02:54 | PLANNED SHUTDOWN | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR SATABARI , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : TRF-1 : VIDHA DHARI SAHURPUR:PM, *TRF-1 : D-2 ANSAL SATBARI:PM*,*TRF-1 : D 21A ANSAL VILLA, SATBARI*, TRF-1 : C-8 ANSAL SATBARI;PM | 515
10 | 15/04/2018 | NGL | 12:22 | 13:34 | 01:11 | HT SYSTEM FAULT | Grid:PASCHIM VIHAR (66/33/11KV) GRID SSTN To Feeder:11kV FDR NILOTHI STP , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : 400 TRF-1*,*400 TRF-1 TAK CHAND COLONY*,*400 TRF-1*,*DEDICATED TO HVDS*,*400 TRF-1:DEEPAK VIHAR*,*400 TRF:NILOTHI VILLAGE STN-1*,*630 TRF-1:NILOTHI VILLAGE STN-2*,*630 TRF-1:SHIV RAM PARK NILOTHI MORE*,*630 TRF-2:DEEPAK VIHAR*,* TRF1:PLM TAK CHAND COLONY-DT-1*,*25 TRF-1: | 534
11 | 15/04/2018 | NGL | 14:19 | 16:03 | 01:44 | EMERGENCY SHUTDOWN | Grid:NANGLOI WATER WORKS (66/11kV) GRID SSTN To Feeder:11 KV FDR SAINI MOHALLA NEAR WATER TANK , LT ACB:TO ATTEND HOT SPOT | RESTORED/ REPAIRED | Part of : *990 TRF-1:Naresh Park Tulsi Wala S/s* | 289
12 | 15/04/2018 | SVR | 15:42 | 17:09 | 01:26 | LT FEEDER | Grid:66/11KV MEETHAPUR GRID SUB STN To Feeder:11kV FDR GYAN MANDIR , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : 630 TRF : GYAN MANDIR | 128
13 | 15/04/2018 | VKJ | 17:30 | 18:55 | 01:24 | HT SYSTEM FAULT | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR MANAGALPURI , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : TRF-1 ANAND GRAM*,*TRF-1 ANANDGRAM PLINTH*,*TRF-1 FARM NO.16 P/M SHAKUNTLA(SWAT HOUSE)*TRF-1 ARUN SINGH (SHAKUNTALA)*,*TRF-1 ST. LTG. NR. SHAKUNTALA FARM*,*TRF-1 ROSA VILLA FARM*,*TRF-1 FARM NO.24 P/M SHAKUNTLA*TRF-1 PETROL PUMP*,*TRF-1 MAUSAM VIBHAG*TRF-1 VKJ404;VKJ404;HERO HONDA (RIKKHI FARM)*,*TRF-1 NAVAL, NEAR ANDHERIA MORE;;TRF-1 ARJUNGARH METRO STATION*TRF-1 P and T, M G ROAD, GHITTORNI*,*TRF-1 FARM NO.19 P/M SHAKUNTLA | 462
14 | 15/04/2018 | TGN | 23:30 | 00:41 | 01:10 | HT SYSTEM FAULT | Grid:MADIPUR (33/11kV) GRID SSTN To Feeder:R-G BLOCK RAGHUBIR NAGAR , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : 630 TRF-1: HMP Colony Raghubir Nagar*,*630 TRF-1 :RG-BLOCK PARKWALA SSTN,RAGHUBIR NGR*,*400TRF-1:B-3,12.5 YARD(PARK) SSTN-2*,*630TRF-2:RG-BLOCK RAGHUBIR NAGAR I/D:ID*,*400TRF-1:B-3,12.5 YARD(PARK) SSTN-2*,*630TRF-1:B-3,12.5 YARD(NALA) SSTN-1 | 478
15 | 16/04/2018 | SKT | 05:34 | 06:41 | 01:07 | HT SYSTEM FAULT | Grid:66kV FATEHPUR BERI GRID To Feeder:11kV FDR O/G NO.-5 RUMALO DEVI , 11KV GRID PANEL,:PROTECTION MALFUNCTION, | RESTORED/ REPAIRED | Part of : TRF-1 GOVT. SCHOOL DERA:PM*TRF-1 MICRO:PM*TRF-1 ANITA SINGH:PM*,*TRF-1 ASTHAL MANDIR*,*TRF-1 BABA MOHALLA DERA VILLAGE*,*TRF-1 VILLAGE DERA:PL*TRF-1 BARI BHATI:PL*,*TRF-1 HARIJAN BASTI DERA:PL*,*TRF-1 BHATIA FARM NEAR F 37 RADHEY MOHAN DRIVE*,*TRF-1 DULI CHAND:PM*,*TRF-1 JASWANTI (BARI BHATI):PM*,*TRF-1 GILL FARM:PM*TRF-1 STREET LIGHT DT ON DERA VILL ROAD*,*TRF-1 ANGURI DEVI STN NEAR DERA CROSSING:PM*,*TRF-1 BABU SINGH:PM | 512
16 | 15/04/2018 | MDK | 21:03 | 24:00 | 2:57 | EHV TRIPPING | DUE TO B/D FROM MUNDKA TO 25MVA PTR-1 | RESTORED/ REPAIRED | BULBUL VATIKA, HIRAN KUDNA, IOCL BOTTLING, BABA HARIDAS | 1396 | FLASH OBSERVED ON 11KV FEEDER(BULBUL VATIKA)