## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## TPDDL BULLETIN
DISCOM : ___TATA Power-DDL_________
OUTAGE REPORT FOR :___08-04-2018___________
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Details
1 | 2018-04-08 | Shalimar Bagh | 07:31 | 08:34 | 0.04375 | HT SYSTEM FAULT | Cat Electrocuted | Restored/Repaired | Parts of : Jahangirpuri | 396 | Interruption due to fault
2 | 2018-04-08 | Mangolpuri | 08:19 | 12:15 | 0.16389 | HT SYSTEM FAULT | HT Conductor Broken | Restored/Repaired | Parts of : Laxmi Vihar | 3775 | Interruption due to fault
3 | 2018-04-08 | Narela | 10:22 | 11:55 | 0.064583 | HT SYSTEM FAULT | Pin Insulator Faulty | Restored/Repaired | Parts of : Tiggipur | 418 | Interruption due to fault
4 | 2018-04-08 | Mangolpuri | 14:40 | 15:55 | 0.052083 | HT SYSTEM FAULT | Birdage | Restored/Repaired | Parts of : Pratap Vihar | 7337 | Interruption due to fault
5 | 2018-04-08 | Bawana | 19:18 | 21:35 | 0.095139 | HVDS CABLE & OTHER SYSTEM | HT ABC Burnt | Restored/Repaired | Parts of : Inder Enclave | 5979 | Interruption due to fault
6 | 2018-04-08 | Badli | 08:35 | 10:30 | 0.079861 | HT SYSTEM FAULT | HT Jumper Burnt | Restored/Repaired | Parts of : Samaypur | 682 | Interruption due to fault
7 | 2018-04-08 | Moti Nagar | 08:02 | 09:30 | 0.061111 | HVDS TRANSFORMER | DD Jumper Burnt | Restored/Repaired | Parts of : Bali Nagar | 1219 | Interruption due to fault
8 | 2018-04-08 | Civil Lines | 08:11 | 09:35 | 0.058333 | HVDS CABLE & OTHER SYSTEM | HT ABC Faulty | Restored/Repaired | Parts of : Kamla Nagar | 1654 | Interruption due to fault
9 | 2018-04-08 | Keshav Puram | 08:43 | 11:40 | 0.12292 | HT SYSTEM FAULT | HT Jumper Burnt | Restored/Repaired | Parts of : Rampura | 325 | Interruption due to fault
10 | 2018-04-08 | Narela | 43198.6312 | 43198.6806 | 0.049306 | HT SYSTEM FAULT | HT Conductor Broken | Restored/Repaired | Parts of : Khera Kalan | 4831 | Interruption due to fault
11 | 2018-04-08 | Bawana | 12:25 | 13:59 | 0.065278 | HVDS CABLE & OTHER SYSTEM | HT ABC Burnt | Restored/Repaired | Parts of : Sukhbir Nagar | 5365 | Interruption due to fault
12 | 2018-04-08 | Mangolpuri | 19:35 | 21:00 | 0.059028 | HT SYSTEM FAULT | Birdage | Restored/Repaired | Parts of : Sultanpuri | 462 | Interruption due to fault
13 | 2018-04-08 | Bawana | 20:31 | 21:55 | 0.058333 | HT SYSTEM FAULT | Guard Wire Broken | Restored/Repaired | Parts of : Kanjhawala | 2411 | Interruption due to fault
14 | 2018-04-08 | Narela | 43198.4229 | 43198.4771 | 0.054167 | HVDS CABLE & OTHER SYSTEM | HT Cable Faulty | Restored/Repaired | Parts of : Sannoth Village | 1145 | Interruption due to fault
15 | 2018-04-08 | Narela | 11:50 | 13:10 | 0.055556 | LT FEEDER | Tyco Box Burnt | Restored/Repaired | Parts of : Prem Nagar | 563 | Interruption due to fault
16 | 2018-04-08 | Shakti Nagar | 18:05 | 19:10 | 0.045139 | LT FEEDER | LT Cable Burnt | Restored/Repaired | Parts of : Shazada Bagh | 462 | Interruption due to fault

## Sheet5 (hidden)
43136.5729 | 43136.6944 | 02:55 | 2:55
43136.4986 | 43136.6583 | 03:50 | 3:50
43136.7722 | 43136.8285 | 01:21 | 1:21
43136.4549 | 43136.7139 | 06:13 | 6:13
43136.4285 | 43136.7118 | 06:48 | 6:48
43136.441 | 43136.684 | 05:50 | 5:50
43136.4479 | 43136.6667 | 05:15 | 5:15
43136.475 | 43136.6625 | 04:30 | 4:30
43136.4243 | 43136.6806 | 06:09 | 6:09
43136.4153 | 43136.7104 | 07:05 | 7:05
43136.6979 | 43136.7486 | 01:13 | 1:13
43136.8778 | 43136.9549 | 01:51 | 1:51
0.45833 | 0.68403 | 05:25 | 5:25
0.55764 | 0.73125 | 4:10 | 4:10
0.68819 | 0.75764 | 1:40 | 1:40
0.49167 | 0.71806 | 5:26 | 5:26

## Sheet4 (hidden)
|  | 43131.4583 | 43131.5174 | 01:25 | 1:25 | 0:00
|  | 43131.6153 | 43131.6667 | 01:14 | 1:14 | 0:00
2018-01-31 | 2018-01-31 14:53 | 43131.5236 | 0.62014 | 02:19 | 2:19 | 0:00
|  | 43131.7222 | 43131.7917 | 01:40 | 1:40 | 0:00
|  | 43131.491 | 43131.7111 | 05:17 | 5:17 | -2.7487e-12
|  | 43131.4479 | 43131.6583 | 05:03 | 5:03 | -3.444e-11
|  | 43131.4458 | 43131.7479 | 07:15 | 7:15 | 0:00
|  | 43131.466 | 43131.7431 | 06:39 | 6:39 | 0:00
|  | 43131.4604 | 43131.7049 | 05:52 | 5:52 | -3.5572e-12
|  | 43131.4368 | 43131.7132 | 06:38 | 6:38 | -1.2935e-12
|  | 43131.4271 | 43131.6667 | 05:45 | 5:45 | -4.8506e-12
|  | 43131.4181 | 43131.7042 | 06:52 | 6:52 | 0:00
|  | 43131.45 | 43131.6285 | 04:17 | 4:17 | -3.2338e-13
|  | 43131.4868 | 43131.5382 | 01:14 | 1:14 | 0:00
|  | 43131.3028 | 43131.3576 | 01:19 | 1:19 | 0:00
|  | 43131.4924 | 44227.5382 | 01:06 | 1096.0458 | 1096
|  | 43131.5757 | 43131.7549 | 04:18 | 4:18 | 0:00
|  | 43131.6014 | 43131.6604 | 01:25 | 1:25 | -4.0422e-12
|  | 43131.5993 | 43131.7222 | 02:57 | 2:57 | -6.7909e-12
|  | 43131.6993 | 43131.7681 | 01:39 | 1:39 | -1.4552e-12
|  | 43131.6674 | 43131.809 | 03:24 | 3:24 | 0:00
|  | 0.33611 | 0.39097 | 1:19 | 1:19 | 0:00
|  | 0.30278 | 0.37847 | 1:49 | 1:49 | 0:00
|  | 0.44583 | 0.59097 | 3:29 | 3:29 | 0:00
|  | 0.72431 | 0.78542 | 1:28 | 1:28 | 0:00
|  | 0.80347 | 0.89583 | 2:13 | 2:13 | 0:00

## Sheet3 (hidden)
43105.5833 | 43105.6319 | 01:10 | 1:10
43105.7257 | 43105.8056 | 01:55 | 1:55
43105.4215 | 43105.7167 | 07:05 | 7:05
43105.4778 | 43105.7083 | 05:32 | 5:32
43105.4618 | 43105.7479 | 06:52 | 6:52
43105.5479 | 43105.625 | 01:51 | 1:51
43105.5035 | 43105.7118 | 05:00 | 5:00
43105.5146 | 43105.6833 | 04:03 | 4:03
43105.4764 | 43105.5667 | 02:10 | 2:10
43105.5257 | 43105.5972 | 01:43 | 1:43
43105.5049 | 43105.625 | 02:53 | 2:53
43105.2021 | 43105.3021 | 02:24 | 2:24
43105.3757 | 43105.4653 | 02:09 | 2:09
43105.4167 | 43105.7042 | 06:54 | 6:54
43105.4347 | 43105.6667 | 05:34 | 5:34
43105.5299 | 43105.6167 | 02:05 | 2:05
43105.5507 | 43105.6215 | 01:42 | 1:42
43105.6049 | 43105.6632 | 01:24 | 1:24
43105.6417 | 43105.7882 | 03:31 | 3:31
43105.8743 | 43105.9479 | 01:46 | 1:46
0.49514 | 0.55417 | 1:25 | 1:25
0.45694 | 0.71389 | 6:10 | 6:10
0.50486 | 0.59653 | 2:12 | 2:12
0.53542 | 0.72222 | 4:29 | 4:29
0.57708 | 0.625 | 1:09 | 1:09

## Sheet2 (hidden)
42976.2569 | 42976.3056 | 01:10 | 1:10
42976.2389 | 42976.2812 | 01:01 | 1:01
42976.241 | 42976.2882 | 01:08 | 1:08
42976.2833 | 42976.3403 | 01:22 | 1:22
42976.3438 | 42976.4035 | 01:26 | 1:26
42976.4896 | 42976.5896 | 02:24 | 2:24
42976.7535 | 42976.7986 | 01:05 | 1:05
42976.4215 | 42976.655 | 05:36 | 5:36
42976.3403 | 42976.5208 | 04:20 | 4:20
42976.4472 | 42976.7087 | 06:16 | 6:17
42976.3208 | 42976.3929 | 01:43 | 1:44
42976.3288 | 42976.3796 | 01:13 | 1:13
42976.3591 | 42976.4029 | 01:03 | 1:03
42976.5701 | 42976.6737 | 02:29 | 2:29
42976.4215 | 42976.5654 | 03:27 | 3:27
42976.5461 | 42976.5916 | 01:05 | 1:06
42976.5975 | 42976.7538 | 03:45 | 3:45
42976.906 | 42976.9657 | 01:26 | 1:26
19:00 | 20:30 | 1:30 | 1:30
13:03 | 17:40 | 4:37 | 4:37
13:55 | 15:22 | 1:27 | 1:27
14:39 | 17:00 | 2:21 | 2:21
15:13 | 16:27 | 1:14 | 1:14
11:18 | 17:05 | 5:47 | 5:47
11:19 | 16:00 | 4:41 | 4:41
12:24 | 14:08 | 1:44 | 1:44
23:05 | 0:17 | 1:12 | -0.95
22:25 | 23:48 | 1:23 | 1:23
13:49 | 15:40 | 1:51 | 1:51