## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 19.04.2018 TO 06:00 HRS OF 20.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 19.04.2018 | DGN | 43209.5152 | 43209.6375 | 2:56 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT POLE BROKEN | BROKEN POLE REPAIRED | DILSHAD GARDEN INDUSTRIAL AREA | 164 | LT POLE BROKEN SAME REPAIRED
2 | 19.04.2018 | DRG | 43209.512 | 43209.5604 | 1:10 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BUL BULI KHANA DARYAGANJ | 55
3 | 19.04.2018 | JLM | 43209.5451 | 43209.6514 | 2:33 | PLANNED SHUTDOWN | PROJECT WORK | POLE SHIFTING WORK CARRIED OUT | VIVEK VIHAR BLOCK- C | 611 | POLE SHIFTING WORK CARRIED OUT
4 | 19.04.2018 | KRN | 43209.4979 | 43209.6717 | 4:10 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | RANI GARDEN-GEETA COLONY | 1078 | NETWORK UPGRADATION WORK
5 | 19.04.2018 | KWN | 43209.434 | 43209.4935 | 1:26 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | ELECTROCUTION OF EXTERNAL ELEMENTS | GALI NO-7, C-BLK DAYALPUR | 310
6 | 19.04.2018 | KWN | 43209.5521 | 43209.6875 | 3:15 | PLANNED SHUTDOWN | LOAD BALANCING WORK | LOAD BALANCING CARRIED OUT | BLOCK A-JOHRI PUR | 1901 | LOAD BALANCING WORK CARRIED OUT
7 | 19.04.2018 | KWN | 43209.5715 | 43209.6353 | 1:32 | HVDS TRANSFORMER | REPLACEMENT OF HVDS TRANSFORMER | 25KVA HVDS TRANSFORMER REPLACED | NALA ROAD AMAR VIHAR KWR | 258
8 | 19.04.2018 | KWN | 43209.5778 | 43209.6423 | 1:33 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK E & F WEST KARAWAL NAGAR | 445
9 | 19.04.2018 | KWN | 43209.5938 | 43209.6431 | 1:11 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME RMOVED | C-BLOCK INDRA VIHAR | 682
10 | 19.04.2018 | KWN | 43209.6358 | 43209.7132 | 1:51 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT | 630KVA T/F REPLACED BY 990KVA TRANSFORMER | KHAJOORI KHAS KWR | 175
11 | 19.04.2018 | KWN | 43209.9477 | 43210.0278 | 1:55 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | B-BLK GALI NO-3, WEST KAMAL VIHAR | 258
12 | 20.04.2018 | KWN | 43210.0278 | 43210.0824 | 1:19 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | B-BLOCK GALI NO 04 PREM VIHAR | 257
13 | 20.04.2018 | KWN | 43210.0408 | 43210.1215 | 1:56 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | C-BLK MUKAND VHR | 250
14 | 19.04.2018 | LNR | 43209.4563 | 43209.5417 | 2:03 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | GURU ANGAD NAGAR EAST-SWASTHYA VIHAR | 641 | NETWORK UPGRADATION WORK
15 | 19.04.2018 | LNR | 43209.5728 | 43209.6528 | 1:55 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | JUMPER FOUND LOOSE SAME ATTENDED | GANESH NAGAR -LNR | 172
16 | 19.04.2018 | NNG | 43209.2822 | 43209.3473 | 1:34 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | B-BLOCK NAND NAGRI | 860
17 | 19.04.2018 | NNG | 43209.4805 | 43209.5306 | 1:12 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | TO ATTEND FAULT IN THE LINE | LT SOCKET DAMAGED SAME REPLACED | E-BLOCK MEET NAGAR | 124
18 | 19.04.2018 | NNG | 43209.4972 | 43209.5718 | 1:48 | LT FEEDER | TO ATTEND FAULT IN THE LINE | DISTRIBUTION BOX FAULTY SAME REPAIRED | M.S.PARK NAND NAGRI | 125
19 | 19.04.2018 | NNG | 43209.6005 | 43209.6813 | 1:56 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | F-BLOCK GTB ENCLAVE | 256
20 | 20.04.2018 | NNG | 43210.0967 | 43210.1753 | 1:53 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT SOCKET DAMAGED SAME REPLACED | BLOCK B1-NAND NAGARI | 9599
21 | 20.04.2018 | NNG | 43210.2053 | 43210.2639 | 1:24 | HT SYSTEM FAULT | TRANSFORMER FUSE BLOWN | TRANSFORMER FUSE REPLACED | BLOCK A-NATHU COLONY | 430
22 | 20.04.2018 | NNG | 43210.2094 | 43210.2701 | 1:27 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK F-BUNKAR VIHAR | 860
23 | 20.04.2018 | NNG | 43210.2102 | 43210.2708 | 1:27 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | PRC BURNT SAME ATTENDED | BLOCK L-SUNDER NAGRI | 750
24 | 19.04.2018 | PHG | 43209.4652 | 43209.5363 | 1:42 | LT FEEDER | FOR ATTENDING HOT POINT | HOT POINT ATTENDED | CHUNA MANDI PAHARGANJ | 125
25 | 19.04.2018 | PHG | 43209.4931 | 43209.6476 | 3:43 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | ARAM NAGAR-SADAR BAZAR | 1770 | O/H CIRCUIT REPLACED BY ARMOURED CABLE
26 | 19.04.2018 | PNR | 43209.4944 | 43209.6805 | 4:28 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK 33-WEST PATEL NAGAR | 192 | NETWORK UPGRADATION WORK
27 | 19.04.2018 | PNR | 43209.4944 | 43209.5998 | 2:32 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK E-WEST PATEL NAGAR | 190 | NETWORK UPGRADATION WORK
28 | 19.04.2018 | PNR | 43209.4944 | 43209.5989 | 2:30 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK 38-WEST PATEL NAGAR | 92 | NETWORK UPGRADATION WORK
29 | 19.04.2018 | PNR | 43209.4944 | 43209.661 | 4:00 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK 15-WEST PATEL NAGAR | 90 | NETWORK UPGRADATION WORK
30 | 19.04.2018 | PNR | 43209.4993 | 43209.5701 | 1:42 | HT SYSTEM FAULT | WIRE DAMAGED DUE TO FIRE ON POLE | DAMAGED WIRE REPAIRED | DMS COLONY PATEL NAGAR | 155
31 | 19.04.2018 | SRD | 43209.5966 | 43209.6923 | 2:18 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT DUE TO HEAVY OIL LEAKAGE | TRANSFORMER REPLACED | 21-BLOCK OLD RAJENDRA NAGAR | 258 | TRANSFORMER REPLACED DUE TO HEAVY OIL LEAKAGE
32 | 19.04.2018 | VSE | 43209.6516 | 43209.7084 | 1:22 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | ELECTROCUTION OF EXTERNAL ELEMENTS | HARIJAN BASTI KONDALI | 69
33 | 19.04.2018 | YVR | 43209.4154 | 43209.5393 | 2:58 | HT SYSTEM FAULT | POLE DAMAGED BY VEHICLE | DAMAGED POLE REPAIRED | T-BLOCK GAUTAMPURI | 170 | POLE DAMAGED BY VEHICLE SAME REPAIRED
34 | 19.04.2018 | YVR | 43209.4493 | 43209.5356 | 2:04 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK C-7 YAMUNA VIHAR | 250 | NETWORK UPGRADATION WORK
35 | 19.04.2018 | YVR | 43209.4705 | 43209.5402 | 1:40 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK B-1 YAMUNA VIHAR | 82
36 | 19.04.2018 | YVR | 43209.4892 | 43209.5351 | 1:06 | HT SYSTEM FAULT | FIRE IN LTAB | LTAB REPAIRED | YAMUNA FLOOD PLAINS YVR | 172
37 | 19.04.2018 | YVR | 43209.5587 | 43209.6158 | 1:22 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | ELECTROCUTION OF EXTERNAL ELEMENTS | ZAFRABAD VILLAGE | 87
38 | 19.04.2018 | YVR | 43209.7146 | 43209.7653 | 1:13 | HT SYSTEM FAULT | TRIPPING | TRANSIENT FAULT | ZERO PUSTA USMANPUR | 966
39 | 19.04.2018 | YVR | 43209.8083 | 43209.9791 | 4:06 | LT FEEDER | TO ATTEND CONSUMER COMPLAINT | CONDUCTOR SNAPPED SAME ATTENDED | ARVIND NAGAR-GAMRI YVR | 186 | CONDUCTOR SNAPPED SAME ATTENDED