## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 20.04.2018 TO 06:00 HRS OF 21.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 20.04.2018 | DGN | 43210.4611 | 43210.7014 | 5:46 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | OLDANPUR-NAVIN SHAHDARA | 272 | NEW LTAB CIRCUIT LAID TO IMPROVE THE NETWORK
2 | 20.04.2018 | DGN | 43210.4779 | 43210.5355 | 1:23 | PLANNED SHUTDOWN | FAULT IN LT CIRCUIT | TO ATTEND FAULT IN LT CIRCUIT | RAM NAGAR-SILAMPUR | 624
3 | 20.04.2018 | DGN | 43210.5489 | 43210.8038 | 6:07 | LT FEEDER | LT CABLE DAMAGED | DAMAGED CABLE REPAIRED | SANSAR COMPOUND-DILSHAD GARDEN | 48 | 2 NO'S OF LT CABLE'S DAMAGED SAME REPAIRED
4 | 20.04.2018 | DGN | 43210.5682 | 43210.6479 | 1:55 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | RAM NAGAR-SILAMPUR | 61
5 | 20.04.2018 | DGN | 43210.9549 | 43211.0361 | 1:57 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME REPAIRED | DDA QUARTERS-POCKET Q DILSHAD GARDEN | 194
6 | 21.04.2018 | DGN | 43211.0174 | 43211.0958 | 1:53 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT | MOBILE TRANSFORMER REPLACED | JHILMIL INDUSTRIAL AREA-JHILMIL COLONY | 73
7 | 20.04.2018 | DRG | 43210.9816 | 43211.0306 | 1:11 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | KAMLA MARKET-AJMERI GATE | 731
8 | 20.04.2018 | JLM | 43210.4688 | 43210.5417 | 1:45 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPLACED | DAYA NAND VIHAR-ANAND VIHAR | 348
9 | 20.04.2018 | KRN | 43210.5215 | 43210.6506 | 3:06 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK 9-DHARAM PURA | 316 | NETWORK UPGRADATION WORK
10 | 20.04.2018 | KWN | 43210.4042 | 43210.4639 | 1:26 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK C-BHAGAT SINGH COLONY | 8840
11 | 20.04.2018 | KWN | 43210.4632 | 43210.5104 | 1:08 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK D-SHRI RAM COLONY | 3431
12 | 20.04.2018 | KWN | 43210.4722 | 43210.5417 | 1:40 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | BLOCK C-KARAWAL NAGAR | 173
13 | 20.04.2018 | KWN | 43210.4986 | 43210.5813 | 1:59 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | BHAGAT NAGAR-DAYALPUR | 1039
14 | 20.04.2018 | KWN | 43210.5322 | 43210.5833 | 1:14 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | JOHRI ENCLAVE-BHAGIRATHI VIHAR | 1403
15 | 20.04.2018 | KWN | 43210.6449 | 43210.7083 | 1:31 | HT SYSTEM FAULT | TRIPPING | HVDS CABLE FAULTY SAME REPAIRED | LIG DDA FLATS-SONIA VIHAR | 172
16 | 20.04.2018 | KWN | 43210.7368 | 43210.8056 | 1:39 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK B PHASE-6 SHIV VIHAR | 5587
17 | 20.04.2018 | KWN | 43210.7431 | 43210.7983 | 1:20 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME REMOVED | BLOCK R-PATEL VIHAR | 1914
18 | 20.04.2018 | KWN | 43210.7674 | 43210.8215 | 1:18 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | PRC BURNT SAME REPLACED | BLOCK B-GARI MANDU | 5333
19 | 20.04.2018 | LNR | 43210.4806 | 43210.6138 | 3:12 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | EAST END ENCLAVE-LAKSHMI NAGAR | 860 | NETWORK UPGRADATION WORK
20 | 20.04.2018 | LNR | 43210.6104 | 43210.6787 | 1:38 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK D-SHAKARPUR KHAS | 1888
21 | 20.04.2018 | MVR | 43210.4764 | 43210.5504 | 1:47 | PLANNED SHUTDOWN | REPLACEMENT OF DAMAGED LTAB | DAMAGED LTAB REPLACED | SHASHI GARDEN-MAYUR VIHAR | 1151
22 | 20.04.2018 | NNG | 43210.3585 | 43210.4232 | 1:33 | LT FEEDER | TO ATTEND FAULT IN THE LINE | CABLE FAULTY AREA BACKFEEDED | BLOCK B-HARDEV PURI | 1767
23 | 20.04.2018 | NNG | 43210.428 | 43210.475 | 1:08 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | SOCKET DAMAGED SAME REPLACED | MANSAROVAR PARK-DURGA PURI | 259
24 | 20.04.2018 | NNG | 43210.4575 | 43210.7604 | 7:16 | HT SYSTEM FAULT | LT CABLE BURNT | LT CABLE REPAIRED | PART OF NATHU COLONY NAND NAGRI | 259 | LT CABLE BURNT SAME REPAIRED.DELAYED DUE TO MULTIPLE FAULT IN THE CABLE
25 | 20.04.2018 | NNG | 43210.5329 | 43210.6111 | 1:53 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK D-HARSH VIHAR | 259
26 | 20.04.2018 | NNG | 43210.6363 | 43210.7077 | 1:43 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK H-SEWA DHAM | 173
27 | 20.04.2018 | NNG | 43210.6461 | 43210.7127 | 1:36 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | NEW MANDOLI INDUSTRIAL AREA | 259
28 | 20.04.2018 | PNR | 43210.4889 | 43210.5575 | 1:39 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK 35-RAMJAS SPORTS COMPLEX | 14
29 | 20.04.2018 | PNR | 43210.4896 | 43210.5572 | 1:37 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | PREM NAGAR-BALJIT NAGAR | 86
30 | 20.04.2018 | PNR | 43210.4903 | 43210.5577 | 1:37 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK F-FAREEDPURI | 24
31 | 20.04.2018 | PNR | 43210.4965 | 43210.5579 | 1:28 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | CHETAN BASTI- BLOCK J-NEHRU NAGAR | 580
32 | 20.04.2018 | VSE | 43210.4486 | 43210.5041 | 1:20 | HT SYSTEM FAULT | FOR ATTENDING HOT SPOT | HOT SPOT ATTENDED | BLOCK A & B-VASUNDHARA ENCLAVE | 2844
33 | 20.04.2018 | VSE | 43210.4792 | 43210.555 | 1:49 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | BLOCK C2-NEW ASHOK NAGAR | 2844
34 | 20.04.2018 | YVR | 43210.4472 | 43210.5437 | 2:19 | PLANNED SHUTDOWN | PROJECT WORK | DAMAGED LTAB REPLACED | BLOCK B-SUBHASH MOHALLA | 871 | LTAB DAMAGED SAME REPLACED
35 | 20.04.2018 | YVR | 43210.4653 | 43210.5164 | 1:14 | PLANNED SHUTDOWN | PROJECT WORK | FPI INSTALLED AT RMU | ZERO PUSTA-USMAN PUR | 154
36 | 20.04.2018 | YVR | 43210.4727 | 43210.5343 | 1:29 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK J-SILAMPUR COLONY | 1634
37 | 20.04.2018 | YVR | 43210.6644 | 43210.7361 | 1:43 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | JUMPER FOUND LOOSE SAME ATTENDED | BLOCK V-GHONDA PATTI CHAUHAN | 11441