## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 26.04.2018 TO 06:00 HRS OF 27.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 26.04.2018 | JLM | 43216.4861 | 43216.6181 | 3:10 | PLANNED SHUTDOWN | PROJECT WORK | FEEDER SHIFTING WORK CARRIED OUT | VISHWAS NAGAR-SHAHDARA | 793 | FEEDER SHIFTING WORK CARRIED OUT
2 | 26.04.2018 | JLM | 43216.5312 | 43216.5833 | 1:15 | PLANNED SHUTDOWN | CABLE END BOX DAMAGED | CABLE END BOX REPLACED | BLOCK E-JHILMIL COLONY | 574
3 | 26.04.2018 | JLM | 43216.5729 | 43216.6806 | 2:35 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | VISHWAS NAGAR EXTENSION | 1076 | NETWORK UPGRADATION WORK
4 | 26.04.2018 | JLM | 43216.6458 | 43216.7188 | 1:45 | PLANNED SHUTDOWN | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | SHARAD VIHAR-ANAND VIHAR | 262
5 | 26.04.2018 | KRN | 43216.4646 | 43216.5694 | 2:31 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | CHAND MOHALLA-RAJGARH COLONY | 656 | NETWORK UPGRADATION WORK
6 | 26.04.2018 | KWN | 43216.4306 | 43216.4861 | 1:20 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | ELECTROCUTION OF EXTERNAL ELEMENTS | YAMUNA FLOOD PLAINS-CHAUHAN PATTI | 5598
7 | 26.04.2018 | KWN | 43216.5028 | 43216.6578 | 3:43 | PLANNED SHUTDOWN | FOR REPLACING DAMAGED HVDS LEAD | DAMAGED HVDS LEAD REPLACED | BLOCK C-MAN SINGH NAGAR | 1925 | HVDS LEAD DAMAGED SAME REPLACED
8 | 26.04.2018 | KWN | 43216.6288 | 43216.6929 | 1:32 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | 33 FUTTA ROAD PHASE -3 SHIV VIHAR | 846
9 | 26.04.2018 | KWN | 43216.75 | 43216.8087 | 1:25 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT LEAD FAULTY SAME REPAIRED | B-BLK MUKUND VIHAR | 165
10 | 26.04.2018 | KWN | 43216.9375 | 43216.9931 | 1:20 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE SAME REMOVED | TUNDA NAGAR-BHAGIRATHI VIHAR | 699
11 | 26.04.2018 | LNR | 43216.5326 | 43216.6181 | 2:03 | PLANNED SHUTDOWN | FOR CONNECTING REPAIRED LT CABLE | REPAIRED LT CABLE ENERGISED | GANESH NAGAR-SHAKARPUR KHAS | 170 | REPAIRED LT CABLE ENERGISED
12 | 27.04.2018 | LNR | 43217.1352 | 43217.215 | 1:55 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | BUSBAR FLASHED SAME ATTENDED | CHITRA VIHAR-SWASTHYA VIHAR | 675
13 | 27.04.2018 | LNR | 43217.1352 | 43217.2104 | 1:48 | HT SYSTEM FAULT | 630KVA TRANSFORMER FAULTY | TRANSFORMER REPLACED | CHITTRA VIHAR LNR | 675
14 | 26.04.2018 | NNG | 43216.373 | 43216.4472 | 1:47 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LTAB FAULTY SAME REPAIRED | CHHAJJUPUR-BABAR PUR | 211
15 | 26.04.2018 | NNG | 43216.4848 | 43216.558 | 1:45 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | BLOCK L-SUNDER NAGRI | 901
16 | 26.04.2018 | NNG | 43216.5919 | 43216.6669 | 1:48 | HVDS CABLE & OTHER SYSTEM | REPLACEMENT OF HVDS TRANSFORMER | 25KVA HVDS TRANSFORMER REPLACED | SABOLI VILLAGE-MANDOLI | 255
17 | 26.04.2018 | NNG | 43216.7595 | 43216.8021 | 1:01 | HT SYSTEM FAULT | HTAB CABLE END BOX DAMAGED | CABLE END BOX REPAIRED | PRATAP NAGAR NNG | 255
18 | 26.04.2018 | PHG | 43216.441 | 43216.5406 | 2:24 | PLANNED SHUTDOWN | PROJECT WORK | TO CONNECT NEW CABLE | MULTANI DHANDA-SADAR BAZAR | 41 | NEW ARMOURED CABLE CONNECTED
19 | 27.04.2018 | PHG | 43217.1352 | 43217.1944 | 1:25 | HT SYSTEM FAULT | TRIPPING | TRANSIENT FAULT | TELI WARA-NAWAB GANJ | 70
20 | 26.04.2018 | PNR | 43216.4778 | 43216.5236 | 1:06 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK E-WEST PATEL NAGAR | 131
21 | 26.04.2018 | PNR | 43216.4792 | 43216.6111 | 3:10 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK 8-WEST PATEL NAGAR | 20 | NETWORK UPGRADATION WORK
22 | 26.04.2018 | SRD | 43216.9264 | 43216.9862 | 1:26 | HT SYSTEM FAULT | TRIPPING | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | AJMAL KHAN PARK SHANKAR ROAD | 1030
23 | 26.04.2018 | SRD | 43216.9264 | 43217.1042 | 4:16 | HT SYSTEM FAULT | 990KVA TRANSFORMER FAULTY | 990KVA TRANSFORMERREPLACED | KHAJOOR ROAD CHHAPPAR WALA | 45 | 990KVA TRANSFORMER FAULTY SAME REPLACED
24 | 27.04.2018 | VSE | 43217.1516 | 43217.2218 | 1:41 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK B-MAYUR VIHAR PHASE III | 621
25 | 26.04.2018 | YVR | 43216.5188 | 43216.6072 | 2:07 | PLANNED SHUTDOWN | PROJECT WORK | NETWORK UPGRADATION WORK | BLOCK C8-YAMUNA VIHAR | 5916 | NETWORK UPGRADATION WORK
26 | 26.04.2018 | YVR | 43216.567 | 43216.6434 | 1:50 | HT SYSTEM FAULT | TRANSFORMER REPLACEMENT DUE TO HEAVY OIL LEAKAGE | TRANSFORMER REPLACED | C-12, YAMUNA VIHAR | 1758
27 | 26.04.2018 | YVR | 43216.7542 | 43216.8056 | 1:14 | HT SYSTEM FAULT | TRIPPING | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK I-BRAHM PURI | 905