## Format
DISCOM : BRPL
OUTAGE REPORT FOR : 22/04/2018 06:00Hr. To 23/04/2018 06:00Hr.
Sr. No. |  | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Area / DT Effected | No. of consumer affected | Remarks
| TYPE | [5 empty] | Main Reason | Detail
1 | HT-BD | 23/04/2018 | SVR | 05:14 | 6:46 | 1:32 | HT SYSTEM FAULT | Grid:MATHURA ROAD (66/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-7 M.C.I.E , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : TRF-1 : S/STN. NO. 7 MCIE*,*TRF-1 : S/ST.NO-2,M.C.I.E., *TRF-1 : B-1/ D-8 MCIE, TRF-1 : A-40 MCIE* | 345
2 | HT-BD | 23/04/2018 | VKP | 04:51 | 06:03 | 01:12 | HT SYSTEM FAULT | Grid:66kV G-5 PAPPANKALAN (MATIALA) GRID To Feeder:11kV FDR N.S.I.T NO.-2 (D.K.ROAD) , TRANSIENT FAULT,:TRANSIENT FAULT | RESTORED/ REPAIRED | Part of : *990 TRF-1:B-BLOCK MOHAN GARDENK1 EXT , TRF : ZAILDAR ENCLAVE KAMAL MODAL SCHOOL | 256
3 | HT-BD | 23/04/2018 | PLM | 04:20 | 05:47 | 01:26 | HT SYSTEM FAULT | Grid:G-2 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:MAHAVEER ENCLEVE, D-3 , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : *TRF : RAJ NAGAR EXTENSION, TRF : MIYANWALI NAGAR BLOCK B & C | 287
4 | HT-BD | 23/04/2018 | VKP | 03:20 | 04:28 | 01:07 | HVDS CABLE & OTHER SYSTEM | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR MOHAN GARDEN , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : *630 TRF-1 : YADAVWALA*,*630 TRF-1:BG BLOCK MOHAN GARDEN | 386
5 | HT-BD | 23/04/2018 | VKP | 03:15 | 04:29 | 01:13 | HVDS CABLE & OTHER SYSTEM | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR C&D BLOCK MOHAN GARDEN , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : *630-TRF-1 NAWADA SCHOOLWALA*,*990 TRF-2: NAWADA SCHOOLWALA* | 378
6 | HT-BD | 23/04/2018 | NJF | 00:08 | 01:28 | 01:20 | HVDS CABLE & OTHER SYSTEM | Grid:DELHI JAL BOARD NAJAFGARH WATER WORKS (66/11) To Feeder:KAPOOR FARM , HVDS,:FIRE ON THE POLE, | RESTORED/ REPAIRED | Part of : * TRF-1: SBI BANK NAGLI DAIRY*,*400 TRF-1:NANGLI VIHAR*,*400 TRF:-NANGLI VIHAR EXTN*,*100 TRF-1:ST LT NANGLI MOOR | 417
7 | HT-BD | 22/04/2018 | JKP | 21:32 | 22:32 | 01:00 | HT SYSTEM FAULT | Grid:HARI NAGAR (66/11kV) GRID SSTN To Feeder:11KV J-BLOCK RAJORY GARDEN , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : *630 TRF-2 :COMMUNITY CENTRE SSTN, PH-1, MYP*,*630 TRF-1 :MALABAR GDN SSTN, RAJOURI GARDEN*,*1000 TRF-1 :D-BLOCK SSTN, RAJOURI GARDEN* | 479
8 | HT-BD | 22/04/2018 | SKT | 19:38 | 20:41 | 01:02 | HT SYSTEM FAULT | Grid:33 kV SHIVALIK GRID To Feeder:11kV FDR F-BLOCK MALVIYA NAGAR , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : *TRF-3 F-BLOCK MALVIYA NAGAR KIOSK:K*,*TRF-2 G-BLOCK MALVIYA NAGAR KIOSK:K*,*TRF-1 H-BLOCK MALVIYA NAGAR KIOSK:K* | 245
9 | HT-BD | 22/04/2018 | JKP | 18:26 | 19:53 | 01:27 | HT SYSTEM FAULT | Grid:MUKHERJEE PARK (33/11kV) GRID SSTN To Feeder:11kV FDR SUBHASH NAGAR , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : *630TRF-1 :5 :BLOCK NO.-5 SSTN, SUBHASH NAGAR*,*400 TRF-2 :BLK NO.-3 (DABOURWALA) SSTN, S.NGR*,*630 TRF-1 :BLOCK NO.-1 SSTN, SUBHASH NAGAR* | 426
10 | HT-BD | 22/04/2018 | NHP | 17:54 | 19:17 | 01:23 | HT SYSTEM FAULT | Grid:OKHLA PHASE-II (33/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-1, OKHLA PHASE-2, FEEDER-2 , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : *TRF-1 S/STN NO-1 OKHLA PH-2:ID*,*TRF-2 S/STN DDA SHED C OKHLA PH-2:ID*,*TRF-1 S/STN NO-S-1 OKHLA PH-2:ID* | 89
11 | LT-BD | 22/04/2018 | KPR | 17:41 | 19:40 | 01:59 | LT FEEDER | Grid:TUGHLAKABAD (33/11kV) GRID SSTN To Feeder:11kV FDR SSTN NO.-1, SANGAM VIHAR, FEEDER NO.-2 PLINTH MOUNTED , SERVICE LINE,:JUMPER LOOSE/BROKEN FROM DB, | RESTORED/ REPAIRED | Part of : *TRF-1 K-BLK,SANGAM VIHAR* | 87
12 | LT-BD | 22/04/2018 | VKP | 17:18 | 18:30 | 01:11 | LT FEEDER | Grid:BODELLA-II GRID To Feeder:11KV 1616-JANTA FLATS HASTSAL , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : *400 TRF-2 : MURANI HASTSAL:PL* | 73
13 | HT-BD | 22/04/2018 | VKJ | 13:25 | 14:44 | 01:18 | HT SYSTEM FAULT | Grid:66kV VASANT KUNJ C-BLK GRID To Feeder:11 KV FDR B-10, S/S NO.-12, VASANT KUNJ , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : *TRF-1 STN-9 SEC-B POCKET-9 VASANT KUNJ; TRF : STN-12A SEC-B POCKET-10 VASANT KUNJ; *TRF-2 SSTN 12,B-10;STN-11 SEC-B POCKET-10 VASANT KUNJ | 378
14 | HT-BD | 22/04/2018 | KPR | 12:55 | 14:03 | 01:07 | HVDS CABLE & OTHER SYSTEM | Grid:TUGHLAKABAD (33/11kV) GRID SSTN To Feeder:11kV FDR G-2 K-19 SANGAM VIHAR , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : *TRF-1 F-BLK SANGAM VIHAR*,*TRF-1: K-BLOCK, SANGAM VIHAR:PL | 298
15 | HT-BD | 22/04/2018 | SVR | 09:22 | 10:46 | 01:24 | HVDS CABLE & OTHER SYSTEM | Grid:MOHAN CO-OPERATIVE (66/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-2 M.B EXTN. , HVDS,:HVDS CABLE FAULTY, | RESTORED/ REPAIRED | Part of : *TRF-1 S/STN. NO. 2 MOLAR BADH EXTN.; TRF : G BLK MOLAR BAND EXTNSANJAY SINGHAL* | 245
16 | HT-BD | 22/04/2018 | TGN | 07:39 | 09:01 | 01:22 | HT SYSTEM FAULT | Grid:CHAUKHANDI (33/11kV) GRID SSTN To Feeder:11 kV FDR TILAK VIHAR , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : *990 TRF-1 :TILAK VIHAR SSTN NO-1,TILAK NGR*,*990 TRF-1 :GALI NO.-9 SSTN, SANTGARH NALEWALA*,*990 TRF-1 :SANT GARH NALE WALA SSTN, SANT GARH | 396
17 | HT-BD | 22/04/2018 | KPR | 06:34 | 07:39 | 01:04 | HT SYSTEM FAULT | Grid:TUGHLAKABAD (33/11kV) GRID SSTN To Feeder:11kV FDR VAYUSENABAD , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : *TRF-1 BSF TIGRI EXTENTION* | 157
18 | HT-BD | 22/04/2018 | SKT | 06:31 | 07:37 | 01:05 | HT SYSTEM FAULT | Grid:33kV D.C.SAKET GRID To Feeder:11kV FDR DMRC VIA ANDHRA SCHOOL S/S+BLIND SCHOOL+PUSHP VIHAR S/S NO.-12 , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : *TRF-1 STN-12 SEC-7 PUSHAP VIHAR:ID*,*TRF-1 : JAI GURU DEV P/M S/STN SEC-6 P. VIHAR*,*TRF-2 STN-14 SEC-7 PUSHAP VIHAR:ID*,*TRF-1 STN-3 SEC-3 PUSHAP VIHAR | 401
19 | HT-BD | 22/04/2018 | PJB | 06:23 | 08:00 | 01:37 | HT SYSTEM FAULT | Grid:MADIPUR (33/11kV) GRID SSTN To Feeder:BOOSTER PUMP PUNJABI BAGH , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : *630 TRF-1: RD. NO.-41(NATHA SINGH VATIKA),PJB*,*630 TRF-1: ROAD NO.-41,NEAR T.T.PARK,PJB*,*630TRF-2:ROAD NO-41(NATHA VATIKA)* | 395
20 | HT-PSD | 22/04/2018 | NGL | 11:00 | 14:10 | 03:10 | PLANNED SHUTDOWN | Grid:UDYOG NAGAR (33/11kV) GRID SSTN To Feeder:11kV FDR F-BLOCK D.S.I.D.C , 11KV FEEDER:CARRY OUT PREVENTIVE MTC | RESTORED/ REPAIRED | Part of : *990 TRF-1 F-BLOCK DSIDC*,*990 TRF-1:I/D OLD B BLK DSIDC*,*630 TRF-1:BHIM NAGAR JJC | 512
21 | HT-PSD | 22/04/2018 | SVR | 11:00 | 14:52 | 03:52 | PLANNED SHUTDOWN | Grid:JAMIA MILIA (33/11kV) GRID SSTN To Feeder:11kV FDR GAFFAR MANZIL , TRANSFORMER:CIVIL WORK | RESTORED/ REPAIRED | Part of : *TRF-1 HAZI COLONY GAFFAR MANZIL | 241
22 | HT-PSD | 22/04/2018 | VKP | 10:58 | 14:35 | 03:36 | PLANNED SHUTDOWN | Grid:BODELLA-II GRID To Feeder:11KV FDR DDA TRANSIT CAMP NO.-2 , HT INTERMEDIATE FEEDER:MAKING OF END BOX | RESTORED/ REPAIRED | Part of : *630 TRF-1:SHIV VIHAR SHANI MARKET*,* TRF-1: SHIV VIHAR J J COLONY NEAR ROAD*,* TRF-1:COL BHATIA FARM*,*400 TRF-1:RAJ HANS :PL* | 456