## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet 1
DISCOM : ___TATA Power-DDL_________
OUTAGE REPORT FOR :___18-04-2018___________
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Details
1 | 2018-04-18 17:38 | Shalimar Bagh | 10:55 | 16:24 | 5:29 | PLANNED SHUTDOWN | HT ABC Replacement | Restored/Repaired | Parts of : Pardhan Enclave | 522 | Planned outage
2 | 2018-04-18 17:38 | Narela | 11:07 | 15:32 | 4:25 | PLANNED SHUTDOWN | Tree Trimming | Restored/Repaired | Parts of : Sannoth Village | 4797 | Planned outage
3 | 2018-04-18 17:38 | Shalimar Bagh | 10:07 | 17:14 | 7:07 | PLANNED SHUTDOWN | HT Line Shifting | Restored/Repaired | Parts of : C Block Jahangirpuri | 1747 | Planned outage
4 | 2018-04-18 17:38 | Mangolpuri | 07:53 | 12:09 | 4:16 | PLANNED SHUTDOWN | DT Maintenance | Restored/Repaired | Parts of : Aman Vihar | 1524 | Planned outage
5 | 2018-04-18 17:38 | Narela | 11:18 | 17:18 | 6:00 | PLANNED SHUTDOWN | HT Pole Replacement | Restored/Repaired | Parts of : Gautam Colony | 3188 | Planned outage
6 | 2018-04-18 17:38 | Mangolpuri | 10:25 | 14:22 | 3:57 | PLANNED SHUTDOWN | For Attending Hot Spot | Restored/Repaired | Parts of : Begampur | 4679 | Planned outage
7 | 2018-04-18 17:38 | Shalimar Bagh | 10:17 | 16:42 | 6:25 | PLANNED SHUTDOWN | For Civil Work | Restored/Repaired | Parts of : Haiderpur Village | 2057 | Planned outage
8 | 2018-04-18 17:38 | Rohini | 09:57 | 13:54 | 3:57 | PLANNED SHUTDOWN | HT Cable Replacement | Restored/Repaired | Parts of : Sec 3 Rohini | 746 | Planned outage
9 | 2018-04-18 17:38 | Narela | 10:24 | 17:13 | 6:49 | PLANNED SHUTDOWN | New RMU Installation | Restored/Repaired | Parts of : Sungerpur | 3225 | Planned outage
10 | 2018-04-18 17:38 | Badli | 14:49 | 16:22 | 1:33 | PLANNED SHUTDOWN | Relay Replacement | Restored/Repaired | Parts of : Samaypur | 1450 | Planned outage
11 | 2018-04-18 17:38 | Rohini | 11:28 | 13:15 | 1:47 | PLANNED SHUTDOWN | DT Meter Replacement | Restored/Repaired | Parts of : Sec 7 Rohini | 771 | Planned outage
12 | 2018-04-18 17:38 | Moti Nagar | 10:50 | 16:28 | 5:38 | PLANNED SHUTDOWN | DT Replacement | Restored/Repaired | Parts of : Inderpuri | 318 | Planned outage
13 | 2018-04-18 17:38 | Narela | 10:36 | 17:50 | 7:14 | PLANNED SHUTDOWN | HT ABC Replacement | Restored/Repaired | Parts of : Shahpur Village | 715 | Planned outage
14 | 2018-04-18 17:38 | Shalimar Bagh | 09:15 | 10:20 | 1:05 | HT SYSTEM FAULT | Guard Wire Broken | Restored/Repaired | Parts of : Mukundpur | 2275 | Interruption due to fault
15 | 2018-04-18 17:38 | Shalimar Bagh | 13:26 | 15:23 | 1:57 | DISTRIBUTION TR. | LT ACB Replacement | Restored/Repaired | Parts of : H Block Jahangirpuri | 2118 | Interruption due to fault
16 | 2018-04-18 17:38 | Narela | 12:00 | 14:00 | 2:00 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire at Pole | Restored/Repaired | Parts of : Bakhtawarpur | 1770 | Force majeure due to fire
17 | 2018-04-18 17:38 | Bawana | 14:31 | 15:50 | 1:19 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | External Object Fell on Line | Restored/Repaired | Parts of : Savda Village | 3188 | Force majeure due to sabotage
18 | 2018-04-18 17:38 | Narela | 18:03 | 19:05 | 1:02 | HVDS CABLE & OTHER SYSTEM | HT Jumper Sparking | Restored/Repaired | Parts of : Nai Basti | 1124 | Interruption due to fault
19 | 2018-04-18 17:38 | Bawana | 18:41 | 19:55 | 1:14 | HVDS CABLE & OTHER SYSTEM | HT Jumper Burnt | Restored/Repaired | Parts of : Rama Vihar | 1983 | Interruption due to fault
20 | 2018-04-18 17:38 | Narela | 17:06 | 18:25 | 1:19 | HT SYSTEM FAULT | HT ABC Burnt | Restored/Repaired | Parts of : Sec A-9 Narela | 2617 | Interruption due to fault
21 | 2018-04-18 17:38 | Bawana | 20:35 | 22:00 | 1:25 | HVDS CABLE & OTHER SYSTEM | Squirrel Electrocuted | Restored/Repaired | Parts of : Ghevra Village | 1292 | Interruption due to fault
22 | 2018-04-18 17:38 | Mangolpuri | 08:11 | 09:20 | 1:09 | HVDS CABLE & OTHER SYSTEM | HT Socket Burnt | Restored/Repaired | Parts of : Nithari Village | 6960 | Interruption due to fault
23 | 2018-04-18 17:38 | Civil Lines | 10:46 | 15:30 | 4:44 | PLANNED SHUTDOWN | Tyco Box Replacement | Restored/Repaired | Parts of : Sangam Park | 681 | System schedule maintenance
24 | 2018-04-18 17:38 | Moti Nagar | 11:37 | 16:30 | 4:53 | PLANNED SHUTDOWN | LT Pole Cleaning | Restored/Repaired | Parts of : Zakhira | 343 | System schedule maintenance
25 | 2018-04-18 17:38 | Shalimar Bagh | 11:53 | 13:15 | 1:22 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Sant Nagar | 322 | System schedule maintenance
26 | 2018-04-18 17:38 | Badli | 12:44 | 14:30 | 1:46 | LT FEEDER | LT ABC Burnt | Restored/Repaired | Parts of : Raja Vihar | 635 | Interruption due to fault
27 | 2018-04-18 17:38 | Narela | 13:00 | 14:10 | 1:10 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Jumper Burnt | Restored/Repaired | Parts of : Holambi Khurd | 359 | Interruption due to fault
28 | 2018-04-18 17:38 | Moti Nagar | 11:05 | 14:25 | 3:20 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Ranjit Nagar | 417 | System schedule maintenance

## Sheet3 (hidden)
43105.5833 | 43105.6319 | 01:10 | 1:10
43105.7257 | 43105.8056 | 01:55 | 1:55
43105.4215 | 43105.7167 | 07:05 | 7:05
43105.4778 | 43105.7083 | 05:32 | 5:32
43105.4618 | 43105.7479 | 06:52 | 6:52
43105.5479 | 43105.625 | 01:51 | 1:51
43105.5035 | 43105.7118 | 05:00 | 5:00
43105.5146 | 43105.6833 | 04:03 | 4:03
43105.4764 | 43105.5667 | 02:10 | 2:10
43105.5257 | 43105.5972 | 01:43 | 1:43
43105.5049 | 43105.625 | 02:53 | 2:53
43105.2021 | 43105.3021 | 02:24 | 2:24
43105.3757 | 43105.4653 | 02:09 | 2:09
43105.4167 | 43105.7042 | 06:54 | 6:54
43105.4347 | 43105.6667 | 05:34 | 5:34
43105.5299 | 43105.6167 | 02:05 | 2:05
43105.5507 | 43105.6215 | 01:42 | 1:42
43105.6049 | 43105.6632 | 01:24 | 1:24
43105.6417 | 43105.7882 | 03:31 | 3:31
43105.8743 | 43105.9479 | 01:46 | 1:46
0.49514 | 0.55417 | 1:25 | 1:25
0.45694 | 0.71389 | 6:10 | 6:10
0.50486 | 0.59653 | 2:12 | 2:12
0.53542 | 0.72222 | 4:29 | 4:29
0.57708 | 0.625 | 1:09 | 1:09

## Sheet2 (hidden)
42976.2569 | 42976.3056 | 01:10 | 1:10
42976.2389 | 42976.2812 | 01:01 | 1:01
42976.241 | 42976.2882 | 01:08 | 1:08
42976.2833 | 42976.3403 | 01:22 | 1:22
42976.3438 | 42976.4035 | 01:26 | 1:26
42976.4896 | 42976.5896 | 02:24 | 2:24
42976.7535 | 42976.7986 | 01:05 | 1:05
42976.4215 | 42976.655 | 05:36 | 5:36
42976.3403 | 42976.5208 | 04:20 | 4:20
42976.4472 | 42976.7087 | 06:16 | 6:17
42976.3208 | 42976.3929 | 01:43 | 1:44
42976.3288 | 42976.3796 | 01:13 | 1:13
42976.3591 | 42976.4029 | 01:03 | 1:03
42976.5701 | 42976.6737 | 02:29 | 2:29
42976.4215 | 42976.5654 | 03:27 | 3:27
42976.5461 | 42976.5916 | 01:05 | 1:06
42976.5975 | 42976.7538 | 03:45 | 3:45
42976.906 | 42976.9657 | 01:26 | 1:26
19:00 | 20:30 | 1:30 | 1:30
13:03 | 17:40 | 4:37 | 4:37
13:55 | 15:22 | 1:27 | 1:27
14:39 | 17:00 | 2:21 | 2:21
15:13 | 16:27 | 1:14 | 1:14
11:18 | 17:05 | 5:47 | 5:47
11:19 | 16:00 | 4:41 | 4:41
12:24 | 14:08 | 1:44 | 1:44
23:05 | 0:17 | 1:12 | -0.95
22:25 | 23:48 | 1:23 | 1:23
13:49 | 15:40 | 1:51 | 1:51