## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 01.07.2018 TO 06:00 HRS OF 02.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 01.07.2018 | KWN | 43282.3125 | 43282.3924 | 1:55 | HVDS CABLE & OTHER SYSTEM | TO ATTEND THE FAULT IN THE LINE | HVDS LEAD BURNT, SAME REPAIRED | BLOCK D-PREM VIHAR,KARAWAL NAGAR. | 820
2 | 01.07.2018 | KWN | 43282.7758 | 43282.85 | 1:47 | HVDS CABLE & OTHER SYSTEM | TO ATTEND THE FAULT IN THE LINE | 3-PHASE HVDS LEAD FAULTY, SAME REPAIRED | BLOCK E-INDIRA VIHAR,JOHRI ENCLAVE-BHAGIRATHI VIHAR. | 820
3 | 01.07.2018 | KWN | 43282.8958 | 43283.0733 | 4:16 | HT SYSTEM FAULT | TO ATTEND THE FAULT IN THE RMU | RMU MECHANISM FOUND FAULTY & ALSO GAS PRESSURE WAS LOW,SAME BYPASSED | WEST KARAWAL NAGAR.KARAWAL NGR EXTN. | 86 | DELAY DUE TO SPACE CONSTRAINTS & LOW GAS PRESSURE IN RMU SAME BYPASSED
4 | 01.07.2018 | LNR | 43282.6293 | 43282.6923 | 1:31 | HT SYSTEM FAULT | TO ATTEND THE FAULT IN THE LINE | HT CABLE FOUND FAULTY, SAME REPAIRED | DHURVA APPARTMENT-MOTHER DAIRY,YAMUNA FLOOD PLAINS-LAXMI NAGAR. | 71
5 | 01.07.2018 | MVR | 43282.7504 | 43282.7986 | 1:09 | LT FEEDER | TO ATTEND THE FAULT IN THE LINE | LT CABLE BURNT, SAME REPAIRED | BLOCK C-GAZIPUR DAIRY FARM,PKT B-MAYUR VIHAR PHASE II. | 392
6 | 02.07.2018 | MVR | 43283.0579 | 43283.1136 | 1:20 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | FIRE ON LT POLE | LT CABLE DAMAGED DUE TO FLASH, SAME REPAIRED | SHANGHTA HOUSE STORE-GAZIPUR DAIRY FARM. | 352
7 | 02.07.2018 | NNG | 43283.0104 | 43283.0857 | 1:48 | LT FEEDER | TO ATTEND THE FAULT IN THE LINE | LTAB BURNT DUE TO FIRE, SAME REPAIRED | BLOCK A-NATHU COLONY,NAND NAGRI. | 1811