## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 04.07.2018 TO 06:00 HRS OF 05.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 04.07.2018 | CCK | 43285.3917 | 43285.488 | 2:19 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | TOWN HALL-KUCHA NATWA | 252 | PREVENTIVE MAINTENANCE CARRIED OUT AT S/STATION UNDER PLANNED SHUT DOWN
2 | 05.07.2018 | DGN | 43286.0014 |  | CONTINUE | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | LT CABLES AND ACB BURNT DUE TO FIRE AT SUB STATION | DAMAGED LT CABLES AND ACB REPLACEMENT WORK IN PROGRESS | PART OF BALBIR NAGAR | 166 | FORCE MAJEURE- FIRE AT S/STN. BALBEER NAGAR. LT CABLE AND LT ACB GOT BURNT
3 | 04.07.2018 | DRG | 43285.4583 | 43285.5032 | 1:05 | PLANNED SHUTDOWN | FOR ATTENDING HOT SPOT | HOT SPOT ATTENDED | DELHI POLICE BHAVAN-PAHARI BHOJLA | 250
4 | 04.07.2018 | KWN | 43285.5245 | 43285.5833 | 1:25 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK E-INDIRA VIHAR | 1020
5 | 04.07.2018 | KWN | 43285.7596 | 43285.895 | 3:15 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | O/H CONDUCTOR SNAPPED SAME ATTENDED | BLOCK F-BHAGIRATHI VIHAR | 145 | HT OVERHEAD CONDUCTOR GOT SNAPPED AT S/STN. F-BLOCK BHAGIRATHI VIHAR
6 | 04.07.2018 | KWN | 43285.9514 | 43286.0964 | 3:29 | DISTRIBUTION TR. | 630KVA TRANSFORMER FAULTY | FAULTY TRANSFORMER REPLACED | BLOCK-E SHRI RAM COLONY | 255 | 630KVA TRANSFORMER GOT FAULTY DUE TO INTERNAL FAULT SAME HAS BEEN REPLACED
7 | 04.07.2018 | LNR | 43285.4257 | 43285.5167 | 2:11 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | RAMESH PARK-LAKSHMI NAGAR | 165 | PREVENTIVE MAINTENANCE CARRIED OUT AT S/STATION UNDER PLANNED SHUT DOWN
8 | 04.07.2018 | LNR | 43285.4264 | 43285.5163 | 2:09 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | VISHWAKARMA PARK-LAKSHMI NAGAR | 170 | PREVENTIVE MAINTENANCE CARRIED OUT AT S/STATION UNDER PLANNED SHUT DOWN
9 | 04.07.2018 | LNR | 43285.4694 | 43285.5165 | 1:08 | PLANNED SHUTDOWN | FOR CONNECTING REPAIRED CABLE | REPAIRED CABLE CONNECTED | SWASTHYA VIHAR-LAXMI NAGAR | 173
10 | 04.07.2018 | PHG | 43285.4201 | 43285.4628 | 1:01 | PLANNED SHUTDOWN | FOR ATTENDING HOT SPOT | HOT SPOT ATTENDED | CHUNA MANDI-PAHAR GANJ | 240
11 | 04.07.2018 | YVR | 43285.4736 | 43285.59 | 2:48 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | ARVIND NAGAR-GHONDA | 170 | PREVENTIVE MAINTENANCE CARRIED OUT AT S/STATION UNDER PLANNED SHUT DOWN
12 | 04.07.2018 | YVR | 43285.4767 | 43285.5436 | 1:36 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE SAME REMOVED | BLOCK B-KONDALI VILLAGE | 1036