## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 05.07.2018 TO 06:00 HRS OF 06.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 05.07.2018 | MVR | 43286.9064 | 43286.9514 | 1:05 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | 13-BLOCK TRILOKPURI | 35
2 | 05.07.2018 | PHG | 43286.4132 | 43286.4714 | 1:24 | PLANNED SHUTDOWN | FOR ATTENDING HOT SPOT | HOT SPOT ATTENDED | BLOCK J-AHATA KEDARA | 1061
3 | 05.07.2018 | SRD | 43286.4201 | 43286.4748 | 1:19 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | PART II- DDA COMPLEX-NEW RAJENDRA NAGAR | 513
4 | 05.07.2018 | YVR | 43286.4806 | 43286.5377 | 1:22 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CHAUHAN BANGAR-JAFFRABAD | 175
5 | 05.07.2018 | YVR | 43286.4938 | 43286.5694 | 1:49 | LT FEEDER | REPLACEMENT OF PIERCING CONNECTOR | PIERCING CONNECTOR REPLACED | B-BLOCK BHAJANPURA | 88
6 | 05.07.2018 | YVR | 43286.6153 | 43286.6715 | 1:21 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | SOCKET BURNT SAME REPLACED | NAYAGAON-NEW KATWARA | 235
7 | 05.07.2018 | YVR | 43286.6493 | 43286.7493 | 2:24 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | JAFFRABAD-MAUJ PUR | 760 | PREVENTIVE MAINTENANCE CARRIED OUT UNDER PLANNED SHUT DOWN
8 | 05.07.2018 | YVR | 43286.8063 | 43287.2104 | 9:42 | HT SYSTEM FAULT | BOTH SOURCE CABLE FAULTY | CABLE REPAIRED | D-BLOCK BHAJANPURA, GAMRI VILLAGE, TIKONA PARK | 250 | CABLE GOT FAULTY DUE TO OVERLOADING AT S/STATION TIKONA PARK AND D-BLOCK GAMRI WHICH HAVING HIGH LOSS OF 74% & 58% RESPECTIVELY