## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 09.07.2018 TO 06:00 HRS OF 10.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 09.07.2018 | JLM | 43290.5039 | 43290.5486 | 1:04 | DISTRIBUTION TR. | FOR ATTENDNING OIL LEAKAGE FROM TRANSFORMER | OIL LEAKAGE PROBLEM ATTENDED | INSTITUTIONAL AREA PREET VIHAR | 45
2 | 09.07.2018 | KWN | 43290.8944 | 43290.9965 | 2:27 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE CIRCUIT | HT SOCKET BURNT SAME REPLACED | HATHI WAALA, NEW SABHAPUR | 863 | HT SOCKET BURNT AT S/STATION HATHI WALA, RMU GOT TRIPPED
3 | 09.07.2018 | KWN | 43290.9167 | 43290.9931 | 1:50 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE CIRCUIT | RMU TRIPPED SAME ATTENDED | ARVIND NAGAR-GHONDA | 1726
4 | 09.07.2018 | LNR | 43290.6356 | 43290.7102 | 1:47 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT | MOBILE TRANSFORMER REPLACED | GANESH NAGAR-SHAKARPUR | 135
5 | 09.07.2018 | MVR | 43290.5639 | 43290.6201 | 1:21 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | LT SOCKET BURNT SAME REPLACED | B-BLOCK KALYANPURI | 42
6 | 09.07.2018 | NNG | 43290.991 | 43291.0549 | 1:32 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | MANDOLI VILLAGE NNG | 992
7 | 09.07.2018 | VSE | 43290.5199 | 43290.5799 | 1:26 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | VASUNDHRA ENCLAVE | 34
8 | 09.07.2018 | YVR | 43290.3507 | 43290.4804 | 3:07 | DISTRIBUTION TR. | 990KVA TRANSFORMER FAULTY | FAULTY TRANSFORMER REPLACED | D-BLOCK GOUTAMPURI | 103 | TRANSFORMER AT S/STATION BRAHAMPURI KHATTEY WALA HAVING HIGH OIL LEAKAGE THROUGH TRANSFORMER TANK WHICH COULD NOT BE ATTENDED AT SITE DUE TO WHICH TRANSFORMER NEED TO BE REPLACED.
9 | 10.07.2018 | YVR | 43291.1389 | 43291.1896 | 1:13 | HT SYSTEM FAULT | TRIPPING | TRANSFORMER FUSE BLOWN SAME REPLACED | MAUJPUR, ZAMALU KA BAGH | 1139
10 | 10.07.2018 | YVR | 43291.1896 | CONTINUE |  | DISTRIBUTION TR. | OIL THEFT FROM 2 NO'S OF TRANSFORMER | REFILLING OF OIL CARRIED OUT | ZAMALU KA BAGH YVR | 215 | OIL THEFT FROM 2 NO'S OF TRANSFORMER AT S/STATION ZAMALU KA BAGH.REFILLING IN PROGRESS