## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 11.07.2018 TO 06:00 HRS OF 12.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 11.07.2018 | DGN | 43292.4191 | 43292.5964 | 4:15 | LT FEEDER | LT CABLE FAULTY | FAULTY CABLE REPAIRED | BLOCK B & E MARKET DILSHAD GARDEN | 173 | LT CABLE FAULTY AT S/STATION LSC B&E MARKET, SITE CONSTRAINT AT S/STATION DURING CABLE REVIVAL WHICH WAS UNDER SEWER LINE.
2 | 11.07.2018 | DGN | 43292.5034 | 43292.5792 | 1:49 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | LT SOCKET BURNT SAME REPLACED | BLOCK R- AADINATH BHAWAN DGN | 168
3 | 11.07.2018 | DGN | 43292.6755 | 43292.7508 | 1:48 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | LT LEAD FAULTY SAME REPAIRED | BLOCK A-JHILMIL INDUSTRIAL AREA | 29
4 | 11.07.2018 | DRG | 43292.4868 | 43292.5337 | 1:07 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | LT LEAD BURNT SAME REPAIRED | DELHI GOVT. STAFF FLATS-PRESS ENCLAVE | 155
5 | 11.07.2018 | PNR | 43292.6147 | 43292.6572 | 1:01 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE SAME REMOVED | THAN SINGH NAGAR, NAI BASTI | 2289
6 | 11.07.2018 | PNR | 43292.6729 | 43292.9375 | 6:21 | DISTRIBUTION TR. | OIL LEAKAGE FROM TRANSFORMER | 990KVA TRANSFORMER FAULTY SAME REPLACED | NAI BASTI-ANAND PARBAT | 1313 | DUE TO OIL LEAKAGE TRANSFORMER GOT DEFECTIVE AT NAGARWALA GHATI ROAD AND SAME HAS BEEN REPLACED.
7 | 11.07.2018 | SRD | 43292.6188 | 43292.6706 | 1:14 | HT SYSTEM FAULT | TRIPPING | CONSUMER HT PANEL FLASHED SAME ATTENDED | BLOCK 29-NAIWALA | 1614
8 | 11.07.2018 | YVR | 43292.525 | 43292.6157 | 2:11 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BHAGAT SINGH MOHALLA YVR | 1114 | PREVENTIVE MAINTENANCE WAS CARRIED OUT AT S/STN. BHAGAT SINGH MOHALLA UNDER PLANNED SHUTDOWN