## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 14.07.2018 TO 06:00 HRS OF 15.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 14.07.2018 | DGN | 43295.4601 | 43295.5382 | 1:53 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME REPAIRED | MAYUR VIHAR EXTENSION | 36
2 | 14.07.2018 | DGN | 43295.4618 | 43295.5396 | 1:52 | LT FEEDER | TREE BRANCHES TOUCHING THE LINE | TREE TRIMMING CARRIED OUT | L & H POCKET-2 DILSHAD GARDEN | 154
3 | 14.07.2018 | DGN | 43295.482 | 43295.5417 | 1:26 | LT FEEDER | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | BLOCK 1-RAM NAGAR GT ROAD | 155
4 | 14.07.2018 | KWN | 43295.2708 | 43295.3453 | 1:47 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT ACB FAULTY SAME ATTENDED | BLOCK C-JAI PRAKASH NAGAR | 1253
5 | 14.07.2018 | LNR | 43295.4467 | 43295.5104 | 1:32 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | PPG INDUSTRIAL AREA | 165
6 | 14.07.2018 | LNR | 43295.5479 | 43295.7634 | 5:10 | DISTRIBUTION TR. | 630KVA TRANSFORMER FAULTY | FAULTY TRANSFORMER REPLACED WITH MOBILE TRANSFORMER | SOUTH GANESH NAGAR | 984 | 630KVA TRANSFORMER FAULTY SAME HAS BEEN REPLACED
7 | 14.07.2018 | MVR | 43295.6086 | 43295.6899 | 1:57 | LT FEEDER | FIRE IN LTAB | LTAB REPAIRED | SHASHI GARDEN-MAYUR VIHAR | 1073
8 | 14.07.2018 | PHG | 43295.6297 | 43295.7757 | 3:30 | LT FEEDER | LT CABLE FAULTY | FAUTY CABLE REPAIRED | MULTANI DANDA, ARYA NAGAR | 425 | LT CABLE FAULTY SAME REPAIRED
9 | 14.07.2018 | PHG | 43295.8432 | 43296.1296 | 6:52 | DISTRIBUTION TR. | 990KVA TRANSFORMER FAULTY | FAULTY TRANSFORMER REPLACED | ARAKSHA ROAD PAHARGANJ | 445 | 990KVA TRANSFORMER FAULTY SAME HAS BEEN REPLACED
10 | 15.07.2018 | VSE | 43296.2328 | 43296.2759 | 1:02 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE SAME REMOVED | KONDALI VILLAGE | 820
11 | 14.07.2018 | YVR | 43295.4854 | 43295.6237 | 3:19 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | JAFFRABAD-MAUJ PUR | 180 | PREVENTIVE MAINTENANCE CARRIED OUT UNDER PLANNED SHUTDOWN
12 | 14.07.2018 | YVR | 43295.6307 | 43295.6762 | 1:06 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | HT SOCKET BURNT SAME REPLACED | BLOCK G-SILAMPUR COLONY | 995