## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 15.07.2018 TO 06:00 HRS OF 16.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 16.07.2018 | CCK | 43297.2097 | 43297.2549 | 1:05 | HT SYSTEM FAULT | TRIPPING | TRANSFORMER HT LEAD DAMAGED, SAME REPLACED | BHAGIRATH PLACE-CHANDNI CHOWK. | 257
2 | 15.07.2018 | DGN | 43296.634 | 43296.7882 | 3:42 | HT SYSTEM FAULT | TRIPPING | HT PANEL BUS BAR FOUND FLASHED, SAME REPAIRED | H BLOCK NAVEEN SHAHDARA. | 2028 | RMU GOT FLASHED AT H BLOCK NAVEEN SHAHDARA DUE TO MOISTURE, AREA WAS BACKFEEDED.
3 | 15.07.2018 | KWN | 43296.5833 | 43296.8576 | 6:35 | DAMAGE BY OTHER AGENCIES | REPLACEMENT OF HVDS POLE | HVDS POLE DAMAGED BY UNKNOWN VEHICLE, SAME REPLACED | CHAMAN PARK,KARAWAL NAGAR. | 879 | HVDS POLE GET DAMAGED BY UNKNOWN VEHICLE AT GALI NO. 3 CHAMAN PARK SAME HAS BEEN REPLACED
4 | 16.07.2018 | MVR | 43297.0391 | 43297.0978 | 1:24 | HT SYSTEM FAULT | TRIPPING | RMU FOUND FLASHED, SAME BYPASSED | NIRMAN APPT. ,KALA VIHAR APPT, PARWANA APPT. | 393
5 | 16.07.2018 | MVR | 43297.0391 | 43297.1056 | 1:36 | HT SYSTEM FAULT | TRIPPING | TRANSIENT FAULT | PKT A,PKT C,PKT-2,PKT-3 MAYUR VIHAR-1 | 3075
6 | 16.07.2018 | MVR | 43297.0983 | 43297.1436 | 1:05 | LT FEEDER | TO BYPASS RMU | RMU FOUND FLASHED, SAME BYPASSED | NIRMAN APPT.MVR. | 64
7 | 15.07.2018 | PNR | 43296.721 | 43296.7701 | 1:11 | HT SYSTEM FAULT | TRIPPING | HT CABLE FAULTY, AREA BACKFEEDED | ANAND PARVAT INDUSTRIAL AREA,GALI-8,9. | 1389
8 | 15.07.2018 | YVR | 43296.4708 | 43296.5417 | 1:42 | LT FEEDER | FOR TAKING LOAD ON REPAIRED CABLE | LTAB SHIFTED ON NEW POLE & ENERGISED | MAUJ PUR COMPLEX 1,TIKONA PARK-BHAJANPURA. | 721
9 | 15.07.2018 | YVR | 43296.629 | 43296.7096 | 1:56 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | REPLACEMENT OF LT ACB | LT ACB FOUND FAULTY, SAME REPLACED | BLOCK E-INDIRA VIHAR,BLOCK H-BHAGIRATHI VIHAR. | 366