## Format
DISCOM : BRPL
OUTAGE REPORT FOR : 05/07/2018 06:00Hr. To 06/07/2018 06:00Hr.
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Area / DT Effected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Detail
1 | 05/07/2018 | MNG | 06:27 | 07:46 | 01:19 | HT SYSTEM FAULT | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR NWADA , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,MOHAN GARDEN BLOCK A,MANSA RAM PARK BLOCK A,MANSA RAM PARK_2 | 696
2 | 05/07/2018 | PLM | 07:10 | 08:19 | 01:08 | HT SYSTEM FAULT | Grid:G-6 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11kV FDR PARADISE APPARTMENT SEC.-9 , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : DWARKA SECTOR 9, | 471
3 | 05/07/2018 | VKP | 07:30 | 09:13 | 01:42 | HT SYSTEM FAULT | Grid:HASTAL (66/11kV) GRID SSTN To Feeder:11KV FDR PRESS ENCLAVE , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : PRESS ENCLAVE | 513
4 | 05/07/2018 | DWK | 07:31 | 09:05 | 01:34 | HT SYSTEM FAULT | Grid:G-15 DWARKA REL. ENERGY GRID SSTN To Feeder:11kV FDR SEC-12 PKT-7 , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : DWARKA SECTOR 11,,DWARKA SECTOR 12 | 563
5 | 05/07/2018 | VKJ | 09:00 | 11:07 | 02:07 | PLANNED SHUTDOWN | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR AIRFORCE , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : SAMALKA,RAJOKRI,KAPASHERA ESTATE, | 487
6 | 05/07/2018 | JFR | 10:10 | 14:05 | 03:55 | PLANNED SHUTDOWN | Grid:JAFFARPUR (66/11kV) GRID SSTN To Feeder:11KV JAFFARPUR , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : ,UJWA_3,UJWA_1,SAMASPUR KHALSA_1 | 516
7 | 05/07/2018 | NJF | 10:30 | 14:37 | 04:07 | PLANNED SHUTDOWN | Grid:G-6 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11kV FDR 810-DDA FLATS SECTOR-26 DWK. (VILLAGE POCHANPUR) , LT CIRCUIT:REPAIR THE DAMAGED WIRES ON THE POLE | RESTORED/ REPAIRED | Part of : DWARKA SECTOR 29_2, | 398
8 | 05/07/2018 | RKP | 10:53 | 12:28 | 01:35 | LT FEEDER | Grid:R.K.PURAM-II (33/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-1, SECTOR-1, R.K PURAM , SERVICE LINE,:JUMPER LOOSE/BROKEN FROM DB, | RESTORED/ REPAIRED | Part of : MOHAMMAD PUR_1, | 51
9 | 05/07/2018 | SVR | 11:00 | 15:20 | 04:20 | PLANNED SHUTDOWN | Grid:SARITA VIHAR (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR ALI VILLAGE , TRANSFORMER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : ,GAYATRI KUNJ | 324
10 | 05/07/2018 | SKT | 11:00 | 17:43 | 06:43 | PLANNED SHUTDOWN | Grid:33kV D.C.SAKET GRID To Feeder:11kV FDR C.C ANUPAM , LT CIRCUIT:NETWORK UPGRADTION WORK | RESTORED/ REPAIRED | Part of : ,SAKET BLOCK D | 250
11 | 05/07/2018 | DWK | 11:13 | 12:23 | 01:09 | HT SYSTEM FAULT | Grid:G-15 DWARKA REL. ENERGY GRID SSTN To Feeder:11kV FDR KM CHOWK , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : DWARKA SECTOR 11,,DWARKA SECTOR 4,DWARKA SECTOR 4 PKT 1,DWARKA SECTOR 5 | 578
12 | 05/07/2018 | MDK | 11:16 | 14:05 | 02:48 | PLANNED SHUTDOWN | Grid:NANGLOI WATER WORKS (66/11kV) GRID SSTN To Feeder:11kV FDR YADAV PARK EXT. , TRANSFORMER:REMOVAL OF MOBILE TRANSFORMER & REPLACEMENT OF NEW TRANSFORMER | RESTORED/ REPAIRED | Part of : ,RAJENDRA PARK EXTN. | 395
13 | 05/07/2018 | NGL | 12:04 | 15:27 | 03:23 | PLANNED SHUTDOWN | Grid:PASCHIM VIHAR (66/33/11KV) GRID SSTN To Feeder:11kV FDR MEERA BAGH + 11kV FDR STP-2 SAYED VILLAGE , LT CIRCUIT:NETWORK UPGRADTION WORK | RESTORED/ REPAIRED | Part of : ,MEERA BAGH | 538
14 | 05/07/2018 | PJB | 12:07 | 16:14 | 04:07 | PLANNED SHUTDOWN | Grid:MADIPUR (33/11kV) GRID SSTN To Feeder:11KV ADASRSH BHAWAN , LT CIRCUIT:REPLACEMENT OF DAMAGE LTAB | RESTORED/ REPAIRED | Part of : ,PUNJABI BAGH WEST | 171
15 | 05/07/2018 | NZD | 12:07 | 14:03 | 01:56 | PLANNED SHUTDOWN | Grid:33kV KILOKARI GRID SSTN To Feeder:11 kV FDR ASHRAM CHOWK VIA JEEVAN NAGAR , LT CIRCUIT:MAINTANCE WORK | RESTORED/ REPAIRED | Part of : ,HARI NAGAR ASHRAM | 41
16 | 05/07/2018 | PJB | 12:07 | 16:13 | 04:06 | PLANNED SHUTDOWN | Grid:PASCHIM PURI (33/11kV) GRID SSTN To Feeder:11KV A-3 DISPENSARY , LT CIRCUIT:NETWORK UPGRADTION WORK | RESTORED/ REPAIRED | Part of : PASCHIM VIHAR BLOCK A3, | 52
17 | 05/07/2018 | UMN | 12:22 | 13:54 | 01:32 | EMERGENCY SHUTDOWN | Grid:BINDAPUR (G-3 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR R & S BLOCK CHANAKYA PLACE , LT CIRCUIT:LAYING OF NEW LTAB | RESTORED/ REPAIRED | Part of : BINDAPUR, | 67
18 | 05/07/2018 | KPR | 12:23 | 13:34 | 01:11 | PLANNED SHUTDOWN | Grid:66kV BATRA GRID To Feeder:11kV FDR S/S NO.-5 DAKSHIN PURI , HT INTERMEDIATE FEEDER:TO SHIFT THE CABLE | RESTORED/ REPAIRED | Part of : ,DAKSHINPURI EXTENSION_2 | 674
19 | 05/07/2018 | NGL | 12:30 | 15:28 | 02:58 | PLANNED SHUTDOWN | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR LAXMI PARK , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : NIHAL VIHAR_1,CHANDAN VIHAR_2,INDER ENCLAVE_2 | 624
20 | 05/07/2018 | PLM | 12:35 | 14:22 | 01:46 | LT FEEDER | Grid:G-2 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11KV MANDIR MARG , LT POLE,:FIRE AT SHAKLE POINTS, | RESTORED/ REPAIRED | Part of : MAHAVIR ENCLAVE PART-1 BLOCK G,G-1A& A1, | 59
21 | 05/07/2018 | MDK | 12:36 | 13:40 | 01:03 | HVDS CABLE & OTHER SYSTEM | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR RAJENDERA PARK , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : JANAK PARK BLOCK WZ,RATAN BAGH_1,PREM NAGAR, | 621
22 | 05/07/2018 | TGN | 13:06 | 15:00 | 01:54 | HT SYSTEM FAULT | Grid:MUKHERJEE PARK (33/11kV) GRID SSTN To Feeder:11 kV FDR CHAUKHANDI , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : PASCHIM VIHAR BLOCK GH14,CHAUKHANDI NAGAR,RAVI NAGAR WZ,KHYALA_2,RAVI NAGAR,D.D.A COLONY,VISHNU GARDEN, | 531
23 | 05/07/2018 | SVR | 13:28 | 15:25 | 01:56 | LT FEEDER | Grid:SARITA VIHAR (66/11kV) GRID SSTN To Feeder:11kV FDR SAHEEN BAGH , SERVICE LINE,:FIRE IN SERVICE LINE, | RESTORED/ REPAIRED | Part of : SHAHEEN BAGH, | 64
24 | 05/07/2018 | SVR | 13:39 | 15:27 | 01:47 | LT FEEDER | Grid:SARITA VIHAR (66/11kV) GRID SSTN To Feeder:11kV FDR THOKAR NO.-5 DHARAM KANTA , SERVICE LINE,:FIRE IN SERVICE LINE, | RESTORED/ REPAIRED | Part of : ABDUL FAZAL ENCLAVE PART I_1, | 68
25 | 05/07/2018 | SVR | 14:07 | 15:24 | 01:17 | PLANNED SHUTDOWN | Grid:MATHURA ROAD (66/11kV) GRID SSTN To Feeder:11 kV FDR A-3 M.C.I.E , RMU:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : HT CONSUMER (MCIE) | 1
26 | 05/07/2018 | PLM | 14:47 | 17:10 | 02:23 | PLANNED SHUTDOWN | Grid:G-6 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11kV FDR BHATTWALA , TRANSFORMER:LEAD REPLACEMENT | RESTORED/ REPAIRED | Part of : RAJ NAGAR EXTENSION_1, | 58
27 | 05/07/2018 | JKP | 14:48 | 16:10 | 01:22 | HT SYSTEM FAULT | Grid:REWARI LINE (220/66/11kV, TRANSCO) GRID (NDPL) To Feeder:11KV B-49 MAYAPURI , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : BLOCK B MAYAPURI,MAYAPURI INDUSTRIAL AREA PHASE I, | 68
28 | 05/07/2018 | VKJ | 15:01 | 16:53 | 01:51 | EMERGENCY SHUTDOWN | Grid:66kV I.A.A.I PALAM GRID To Feeder:11 kV FDR MEHRAM NAGAR , LT CIRCUIT:LOAD BALANCING | RESTORED/ REPAIRED | Part of : BLOCK A MAHIPAL PUR EXTN.,MAHIPAL PUR EXTN.,MAHIPAL PUR, | 44
29 | 05/07/2018 | DWK | 15:11 | 16:34 | 01:23 | HT SYSTEM FAULT | Grid:PAPPANKALAN-II (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR P.P SECTOR-17 , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : SEC-17 PKT-A SARVAHIT APPT, SEC-17 PKT-B3 PLOTTED AREA NR CSCI,NO.2 PLOTTED AREA SEC-17 NR SEC-17A | 534
30 | 05/07/2018 | MNG | 15:11 | 16:37 | 01:25 | HT SYSTEM FAULT | Grid:DELHI JAL BOARD NAJAFGARH WATER WORKS (66/11) To Feeder:11KV FDR RAMA PARK , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : VIJAY BLK MOHAN GARDEN,POLICE POST NJF DRAIN VIPIN GDN,VIPIN GDN NEAR SNATAN DHARM MANDIR | 559
31 | 05/07/2018 | VKJ | 15:20 | 16:48 | 01:27 | HT SYSTEM FAULT | Grid:66kV I.A.A.I PALAM GRID To Feeder:11 kV FDR GMR OPPOSITE PALAM GRID , HT O/H,:INSULATOR BROKEN/PUNCTURED, | RESTORED/ REPAIRED | Part of : TRILOK COLONY,BLOCK A MAHIPAL PUR EXTN.,MILAKPUR KOHI RANGPURI,MAHIPAL PUR EXTN.,MAHIPAL PUR VILLAGE,RANG PURI,SHAHABAD MOHAMMADPUR_1,MAHIPAL PUR, | 542
32 | 05/07/2018 | NGL | 15:28 | 16:46 | 01:17 | HT SYSTEM FAULT | Grid:PASCHIM PURI (33/11kV) GRID SSTN To Feeder:11kV FDR UDYOG NGR FEEDER-1 (BHERA ENCLAVE) , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : ,BHERA ENCLAVE | 684
33 | 05/07/2018 | UMN | 15:30 | 17:07 | 01:36 | HT SYSTEM FAULT | Grid:BINDAPUR (G-3 PPK) (66/11kV) GRID SSTN To Feeder:11KV FDR O-BLOCK UTTAM NAGAR , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : NEW UTTAM NAGAR,,VISHWAS PARK_1 | 701
34 | 05/07/2018 | TGN | 15:31 | 17:18 | 01:47 | HT SYSTEM FAULT | Grid:VISHAL (33/11kV) GRID SSTN To Feeder:11kV FDR S-BLOCK VISHNU GARDEN VI WORK CENTER , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : TAGORE GARDEN EXTN BLOCK C,,TAGORE GARDEN EXTENSION,RAGHUBIR NAGAR_1 | 538
35 | 05/07/2018 | PLM | 15:33 | 17:03 | 01:29 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11kV FDR S.P.G , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,SPG COMPLEX | 425
36 | 05/07/2018 | VKJ | 15:35 | 17:04 | 01:29 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR VILLAGE SAHIBABAD MOHD. PUR , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : SHAHABAD MOHAMMADPUR_1,IGI AIRPORT_2, | 435
37 | 05/07/2018 | UMN | 15:35 | 17:33 | 01:58 | HT SYSTEM FAULT | Grid:BINDAPUR (G-3 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR R & S BLOCK CHANAKYA PLACE , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : BINDAPUR,,MAHAVIR ENCLAVE PART III | 678
38 | 05/07/2018 | VKJ | 15:36 | 17:24 | 01:48 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR NAVAL KAPASHERA , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : FARM HOUSE VASANT KUNJ_1,PALAM FARMS_2,BIJAWASAN,SALAPUR KHERA VILLAGE,PALAM FARMS_1,MAYA ENCLAVE BLOCK D A,KAPAS HERA,KAPASHERA ESTATE, | 502
39 | 05/07/2018 | VKJ | 15:37 | 17:28 | 01:50 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR INTERCONNECTOTR NO.-1 (KAPASHERA) , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : ,SAMALAKA EXT BLOCK B,SAMALAKA EXT BLOCK A_1 | 487
40 | 05/07/2018 | VKJ | 15:38 | 17:34 | 01:55 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR JAI SINGH , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : HINDUSTAN PETOLIUM(HTC) | 1
41 | 05/07/2018 | VKJ | 15:38 | 17:30 | 01:52 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR HINDUSTAN PETROLIUM , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : BIJAWASAN_3,,KAPAS HERA | 468
42 | 05/07/2018 | VKJ | 15:39 | 17:30 | 01:50 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR BIJWASAN , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : ,PALAM FARMS_2 | 502
43 | 05/07/2018 | NJF | 15:41 | 17:21 | 01:39 | HT SYSTEM FAULT | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11kV FDR BAMNAULI , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : RAGHUPUR,KANGAM HERI_1,BADU SARAI_1,NANAK HERI_2,NANAK HERI_1,BIJAWASAN_1,DWARKA SECTOR 27,,BSF CAMP CHHAWLA,BIJAWASAN_2 | 674
44 | 05/07/2018 | SVR | 15:41 | 17:41 | 02:00 | HT SYSTEM FAULT | Grid:MATHURA ROAD (66/11kV) GRID SSTN To Feeder:11kV FDR OKHLA SEWAGE , DISTRIBUTION TRANSFORMER,:GARBAGE DUMPING IN S/STN, | RESTORED/ REPAIRED | Part of : BHAGWAN DAS COLONY BLOCK C, | 632
45 | 05/07/2018 | VKJ | 15:42 | 17:35 | 01:52 | HT SYSTEM FAULT | Grid:66kV I.A.A.I PALAM GRID To Feeder:11 kV FDR WESTERN GREEN , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : SAMALKA,RAJOKRI, | 214
46 | 05/07/2018 | SVR | 15:45 | 17:42 | 01:57 | HT SYSTEM FAULT | Grid:EAST OF KAILASH (33/11kV) GRID SSTN To Feeder:11kV FDR SRINIWASHPURI , DISTRIBUTION TRANSFORMER,:GARBAGE DUMPING IN S/STN, | RESTORED/ REPAIRED | Part of : SRI NIWAS PURI EXTENSION,,SRINIWASPURI BLOCK D,SRINIWASPURI BLOCK B,ARMY AREA SHANKAR VIHAR_3 | 624
47 | 05/07/2018 | SVR | 15:55 | 17:30 | 1:35 | HT SYSTEM FAULT | Grid:MATHURA ROAD (66/11kV) GRID SSTN To Feeder:11kV FDR SUKHDEV VIHAR O/H , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : PERIYAR JASOLA DP,NOIDA ROAD ST. LIG- 1 D.P.1,JASOLA PETROL PUMP AUTO YARD,STREET LIGHT SAVITA VIHAR-2,CNG GAS FILLING NOIDA ROAD,SARITA VIHAR FLY OVER | 73
48 | 05/07/2018 | NZD | 15:59 | 17:24 | 01:24 | HT SYSTEM FAULT | Grid:LAJPAT NAGAR-III (33/11kV) GRID SSTN To Feeder:M-BLOCK LAJPAT NAGAR-2 , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : LAJPAT NAGAR PART II,,LAJPAT NAGAR PART II BLOCK M,VINOBA PURI,LAJPAT NAGAR PART III BLOCK O | 429
49 | 05/07/2018 | TGN | 16:00 | 17:21 | 01:20 | HT SYSTEM FAULT | Grid:BODELLA-II GRID To Feeder:11 KV FDR MBS NAGAR , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : GURU NANAK NAGAR,,SAHPURA_1,SANT GARH,PRITHVI PARK | 536
50 | 05/07/2018 | SVR | 16:05 | 18:00 | 1:55 | HT SYSTEM FAULT | Grid:SARITA VIHAR (66/11kV) GRID SSTN To Feeder:11kV FDR G-4, SHAHEEN BAGH , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : SHAHEEN BAGH,JANAK PARK BLOCK CC, | 547
51 | 05/07/2018 | VKJ | 17:10 | 18:15 | 01:05 | HT SYSTEM FAULT | Grid:66kV I.A.A.I PALAM GRID To Feeder:11 kV FDR RAJOKARI , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : DTC COLONY HARI NAGAR, | 138
52 | 05/07/2018 | KPR | 18:05 | 19:21 | 01:16 | HT SYSTEM FAULT | Grid:TUGHLAKABAD (33/11kV) GRID SSTN To Feeder:11kV FDR G-2 K-19 SANGAM VIHAR , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : SANGAM VIHAR BLOCK G-1,,SANGAM VIHAR BLOCK H,TALIMABAD,SANGAM VIHAR BLOCK E,SANGAM VIHAR BLOCK K | 612
53 | 05/07/2018 | JKP | 18:52 | 20:24 | 01:31 | HT SYSTEM FAULT | Grid:D.C. JANAKPURI (33/11kV) GRID SSTN To Feeder:11KV DISTRICT SERVICE CENTRE JANAKPURI , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : JANAKPURI DISTRICT CENTRE, | 135
54 | 05/07/2018 | VKJ | 19:41 | 20:46 | 01:05 | HT SYSTEM FAULT | Grid:VASANT KUNJ (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11 KV FDR I.A.A.I COLONY , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : BIJAWASAN,PALAM FARMS_1,HARI KUNJ,BLOCK L,MILAKPUR KOHI RANGPURI, | 534
55 | 05/07/2018 | NHP | 19:50 | 22:53 | 03:02 | EMERGENCY SHUTDOWN | Grid:EAST OF KAILASH (33/11kV) GRID SSTN To Feeder:11kV FDR SAI PLAZA , TRANSFORMER:OIL TOP UP | RESTORED/ REPAIRED | Part of : KALKAJI, | 39
56 | 05/07/2018 | NZD | 20:09 | 21:33 | 01:23 | HT SYSTEM FAULT | Grid:33kV NIZAMUDDIN GRID To Feeder:11kV FDR SUNDER NAGAR , 11KV GRID PANEL,:CT MOISTURE / DAMAGED, | RESTORED/ REPAIRED | Part of : ,SUNDAR NAGAR | 452
57 | 06/07/2018 | NZD | 01:04 | 02:18 | 01:13 | HT SYSTEM FAULT | Grid:LAJPAT NAGAR-III (33/11kV) GRID SSTN To Feeder:F-BLOCK LAJPAT NAGAR LPN.-1 , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : LAJPAT NAGAR PART I BLOCK H,LAJPAT NAGAR PART I,,LAJPAT NAGAR PART I BLOCK F | 514
58 | 06/07/2018 | VKJ | 03:31 | 04:53 | 01:21 | EMERGENCY SHUTDOWN | Grid:66kV I.A.A.I PALAM GRID To Feeder:11 kV FDR WESTERN GREEN , HT INTERMEDIATE FEEDER:TREE TRIMMING | RESTORED/ REPAIRED | Part of : SAMALKA,RAJOKRI, | 278