## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet 1
DISCOM : ___TATA Power-DDL_________
OUTAGE REPORT FOR :___03-07-2018___________
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Details
1 | 2018-07-03 | Badli | 04:50 | 05:57 | 0.046528 | HT SYSTEM FAULT | HT Jumper Burnt | Restored/Repaired | Parts of : Jain Colony | 2829 | Interruption due to fault
2 | 2018-07-03 | Bawana | 18:26 | 19:30 | 0.044444 | HVDS CABLE & OTHER SYSTEM | HT Cable Faulty | Restored/Repaired | Parts of : Inder Enclave | 6963 | Interruption due to fault
3 | 2018-07-03 | Badli | 01:11 | 02:40 | 0.061806 | DISTRIBUTION TR. | DD Unit Flashed | Restored/Repaired | Parts of : Libaspur Village | 579 | Interruption due to fault
4 | 2018-07-03 | Shalimar Bagh | 00:29 | 01:42 | 0.050694 | HT SYSTEM FAULT | Birdage | Restored/Repaired | Parts of : Sant Nagar | 1094 | Interruption due to fault
5 | 2018-07-03 | Shalimar Bagh | 00:15 | 02:25 | 0.090278 | HVDS CABLE & OTHER SYSTEM | HT ABC Faulty | Restored/Repaired | Parts of : Mahindra Park | 335 | Interruption due to fault
6 | 2018-07-03 | Civil Lines | 02:30 | 06:50 | 0.18056 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | DT Faulty,Mobile Installation Delayed Due to Accessibility Issue | Restored/Repaired | Parts of : Civil Lines | 410 | Force majeure due to accessibility issue
7 | 2018-07-03 | Shakti Nagar | 19:52 | 21:09 | 0.053472 | HT SYSTEM FAULT | Birdage | Restored/Repaired | Parts of : Gulabi Bagh | 518 | Interruption due to fault
8 | 2018-07-03 | Shalimar Bagh | 04:20 | 05:35 | 0.052083 | HT SYSTEM FAULT | Cat Electrocution | Restored/Repaired | Parts of : Bhalswa Village | 2474 | Interruption due to fault
9 | 2018-07-03 | Bawana | 05:11 | 09:02 | 0.16042 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Tree Branch Fell on Line | Restored/Repaired | Parts of : Agar Nagar | 6624 | Force majeure due to sabotage
10 | 2018-07-03 | Model Town | 07:22 | 08:50 | 0.061111 | HT SYSTEM FAULT | HT Socket Burnt | Restored/Repaired | Parts of : Kewal Park | 3287 | Interruption due to fault
11 | 2018-07-03 | Bawana | 10:02 | 11:30 | 0.061111 | HT SYSTEM FAULT | HT Jumper Burnt | Restored/Repaired | Parts of : Mubarakpur Village | 11201 | Interruption due to fault
12 | 2018-07-03 | Badli | 10:04 | 11:38 | 0.065278 | HT SYSTEM FAULT | HT Jumper Sparking | Restored/Repaired | Parts of : Deep Vihar | 2064 | Interruption due to fault
13 | 2018-07-03 | Bawana | 10:36 | 12:19 | 0.071528 | HT SYSTEM FAULT | HT ABC Faulty | Restored/Repaired | Parts of : Auchandi Village | 2712 | Interruption due to fault
14 | 2018-07-03 | Shalimar Bagh | 10:53 | 12:08 | 0.052083 | DISTRIBUTION TR. | For Mobile DT Removal | Restored/Repaired | Parts of : Tomar Colony | 1287 | Interruption due to fault
15 | 2018-07-03 | Bawana | 11:43 | 13:09 | 0.059722 | HT SYSTEM FAULT | Animal Electrocuted | Restored/Repaired | Parts of : Sec-4 DSIDC Bawana | 8776 | Interruption due to fault
16 | 2018-07-03 | Narela | 14:32 | 16:17 | 0.072917 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Feeder Switched Off Due To Fire Message | Restored/Repaired | Parts of : Metro Vihar Ph-1 | 1355 | Force majeure due to fire
17 | 2018-07-03 | Bawana | 16:13 | 17:19 | 0.045833 | HT SYSTEM FAULT | GO Switch Sparking | Restored/Repaired | Parts of : Daryapur Village | 3242 | Interruption due to fault
18 | 2018-07-03 | Bawana | 17:11 | 18:45 | 0.065278 | HVDS CABLE & OTHER SYSTEM | HT Cable Faulty | Restored/Repaired | Parts of : Bawana Village | 424 | Interruption due to fault
19 | 2018-07-03 | Narela | 17:31 | 19:52 | 0.097917 | DAMAGE BY OTHER AGENCIES | HT Pole Broken by Unknown Vehicle | Restored/Repaired | Parts of : Hiranki Village | 1781 | Force majeure due to sabotage
20 | 2018-07-03 | Model Town | 17:06 | 18:15 | 0.047917 | HT SYSTEM FAULT | HT Jumper Burnt | Restored/Repaired | Parts of : Indra Vihar | 1740 | Interruption due to fault
21 | 2018-07-03 | Narela | 18:17 | 19:34 | 0.053472 | HT SYSTEM FAULT | Birdage | Restored/Repaired | Parts of : Gautam Colony | 1791 | Interruption due to fault
22 | 2018-07-03 | Narela | 11:30 | 14:10 | 0.11111 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | External Object fell on Line | Restored/Repaired | Parts of : Tigipur Village | 2667 | Force majeure due to sabotage
23 | 2018-07-03 | Model Town | 10:59 | 13:05 | 0.0875 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire at Pole | Restored/Repaired | Parts of : Old Bhai Parmanand | 656 | Force majeure due to fire
24 | 2018-07-03 | Narela | 0.88542 | 0.99931 | 0.11389 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Tree Branch Fell on Line | Restored/Repaired | Parts of : Ibrahimpur Village | 2678 | Force majeure due to sabotage
25 | 2018-07-03 | Narela | 21:51 | 0.99931 | 0.088889 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Tripping Due to Rain | Restored/Repaired | Parts of : Darshan Vihar | 5342 | Force majeure due to rain
26 | 2018-07-03 | Narela | 13:58 | 0.64583 | 0.063889 | LT FEEDER | IPC Burnt | Restored/Repaired | Parts of : Nangli | 506 | Interruption due to fault
27 | 2018-07-03 | Mangol Puri | 22:35 | 0.99931 | 0.058333 | LT FEEDER | LT Jumper Burnt | Restored/Repaired | Parts of : Budh Vihar | 394 | Interruption due to fault
28 | 2018-07-03 | Narela | 22:37 | 0.99931 | 0.056944 | LT FEEDER | LT Jumper Burnt | Restored/Repaired | Parts of : Gulabi Bagh | 355 | Interruption due to fault
29 | 2018-07-03 | Mangol Puri | 11:22 | 0.66667 | 0.19306 | DAMAGE BY OTHER AGENCIES | LT ABC Damaged by Unknown Vehicle | Restored/Repaired | Parts of : C Block Sultanpuri | 402 | Force majeure due to sabotage
30 | 2018-07-03 | Rohini | 11:51 | 13:43 | 0.077778 | LT FEEDER | LT Cable Faulty | Restored/Repaired | Parts of : Rajapur Village | 320 | Interruption due to fault
31 | 2018-07-03 | Shalimar Bagh | 12:22 | 0.63889 | 0.12361 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Ishu Vihar | 690 | Scheduled system outage
32 | 2018-07-03 | Shalimar Bagh | 12:44 | 0.70139 | 0.17083 | PLANNED SHUTDOWN | Replacement of LT ABC | Restored/Repaired | Parts of : A Block Jahangirpuri | 422 | Scheduled system outage
33 | 2018-07-03 | Civil Lines | 13:23 | 15:47 | 0.1 | PLANNED SHUTDOWN | Tyco Box Replacement | Restored/Repaired | Parts of : New Timarpur | 301 | Scheduled system outage
34 | 2018-07-03 | Badli | 13:36 | 17:58 | 0.18194 | PLANNED SHUTDOWN | LT Bus Bar Replacement | Restored/Repaired | Parts of : Badli Village | 751 | Scheduled system outage
35 | 2018-07-03 | Moti Nagar | 18:20 | 19:25 | 0.045139 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | Tyco Box Burnt | Restored/Repaired | Parts of : Krishi Kunj | 748 | Interruption due to fault

## Sheet3 (hidden)
43105.5833 | 43105.6319 | 01:10 | 1:10
43105.7257 | 43105.8056 | 01:55 | 1:55
43105.4215 | 43105.7167 | 07:05 | 7:05
43105.4778 | 43105.7083 | 05:32 | 5:32
43105.4618 | 43105.7479 | 06:52 | 6:52
43105.5479 | 43105.625 | 01:51 | 1:51
43105.5035 | 43105.7118 | 05:00 | 5:00
43105.5146 | 43105.6833 | 04:03 | 4:03
43105.4764 | 43105.5667 | 02:10 | 2:10
43105.5257 | 43105.5972 | 01:43 | 1:43
43105.5049 | 43105.625 | 02:53 | 2:53
43105.2021 | 43105.3021 | 02:24 | 2:24
43105.3757 | 43105.4653 | 02:09 | 2:09
43105.4167 | 43105.7042 | 06:54 | 6:54
43105.4347 | 43105.6667 | 05:34 | 5:34
43105.5299 | 43105.6167 | 02:05 | 2:05
43105.5507 | 43105.6215 | 01:42 | 1:42
43105.6049 | 43105.6632 | 01:24 | 1:24
43105.6417 | 43105.7882 | 03:31 | 3:31
43105.8743 | 43105.9479 | 01:46 | 1:46
0.49514 | 0.55417 | 1:25 | 1:25
0.45694 | 0.71389 | 6:10 | 6:10
0.50486 | 0.59653 | 2:12 | 2:12
0.53542 | 0.72222 | 4:29 | 4:29
0.57708 | 0.625 | 1:09 | 1:09

## Sheet2 (hidden)
42976.2569 | 42976.3056 | 01:10 | 1:10
42976.2389 | 42976.2812 | 01:01 | 1:01
42976.241 | 42976.2882 | 01:08 | 1:08
42976.2833 | 42976.3403 | 01:22 | 1:22
42976.3438 | 42976.4035 | 01:26 | 1:26
42976.4896 | 42976.5896 | 02:24 | 2:24
42976.7535 | 42976.7986 | 01:05 | 1:05
42976.4215 | 42976.655 | 05:36 | 5:36
42976.3403 | 42976.5208 | 04:20 | 4:20
42976.4472 | 42976.7087 | 06:16 | 6:17
42976.3208 | 42976.3929 | 01:43 | 1:44
42976.3288 | 42976.3796 | 01:13 | 1:13
42976.3591 | 42976.4029 | 01:03 | 1:03
42976.5701 | 42976.6737 | 02:29 | 2:29
42976.4215 | 42976.5654 | 03:27 | 3:27
42976.5461 | 42976.5916 | 01:05 | 1:06
42976.5975 | 42976.7538 | 03:45 | 3:45
42976.906 | 42976.9657 | 01:26 | 1:26
19:00 | 20:30 | 1:30 | 1:30
13:03 | 17:40 | 4:37 | 4:37
13:55 | 15:22 | 1:27 | 1:27
14:39 | 17:00 | 2:21 | 2:21
15:13 | 16:27 | 1:14 | 1:14
11:18 | 17:05 | 5:47 | 5:47
11:19 | 16:00 | 4:41 | 4:41
12:24 | 14:08 | 1:44 | 1:44
23:05 | 0:17 | 1:12 | -0.95
22:25 | 23:48 | 1:23 | 1:23
13:49 | 15:40 | 1:51 | 1:51