## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 19.07.2018 TO 06:00 HRS OF 20.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 19.07.2018 | CCK | 43300.8125 | 43300.9316 | 2:52 | DISTRIBUTION TR. | 990KVA TRANSFORMER FAULTY | TRANSFORMER REPLACED | CM ROAD, MAHAVEER BAZAAR | 279 | 990KVA TRANSFORMER FAULTY AREA BACKFEEDED.
2 | 19.07.2018 | DGN | 43300.7285 | 43300.8097 | 1:57 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | LT LEAD FAULTY SAME REPAIRED | SHMBHU NATH COMPOUND SHAHDRA | 138
3 | 19.07.2018 | DRG | 43300.5024 | 43300.5553 | 1:16 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | LT SOCKET BURNT SAME REPLACED | COMMUNITY CENTRE-JAMA MASZID | 1717
4 | 19.07.2018 | JLM | 43300.5312 | 43300.625 | 2:15 | HT SYSTEM FAULT | HT JUMPER SNAPPED | HT JUMPER REPLACED | GALI NO-2 & 3 VISHWAS NAGAR | 286 | HT JUMPER SNAPPED SAME REPLACED
5 | 19.07.2018 | KWN | 43300.3924 | 43300.4593 | 1:36 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | SHRI RAM COLONY | 702
6 | 19.07.2018 | KWN | 43300.6674 | 43300.734 | 1:36 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE CIRCUIT | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK D-OLD MUSTAFABAD | 604
7 | 19.07.2018 | KWN | 43300.7844 | 43300.8333 | 1:10 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAKDOWN BECAUSE OF HEAVY RAIN AND WATER LOGGING | WATER LOGGED AT S/STATION SAME REMOVED | BLOCK C-MAN SINGH NAGAR | 2799
8 | 19.07.2018 | KWN | 43300.8063 | 43300.8611 | 1:19 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAKDOWN BECAUSE OF HEAVY RAIN AND WATER LOGGING | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK A-BABU NAGAR | 8402
9 | 20.07.2018 | KWN | 43301.0042 | 43301.1299 | 3:01 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | BOTH SOURCE CABLE FAULTY SAME REPAIRED | PART OF A BLOCK DYALPUR | 783 | BOTH SOURCE LT CABLE FAULTY SAME REPAIRED
10 | 19.07.2018 | NNG | 43300.7785 | 43300.8264 | 1:09 | HT SYSTEM FAULT | TRIPPING | TRANSFORMER FUSE BLOWN SAME REPLACED | DDA LIG FLATS LONI ROAD | 863
11 | 19.07.2018 | PHG | 43300.6186 | 43300.6844 | 1:35 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | SERVICE LINE DAMAGED DUE TO FIRE ON POLE | DAMAGED SERVICE LINE REPLACED | AMRIT KAUR MARKET-PAHAR GANJ | 175
12 | 19.07.2018 | PHG | 43300.6854 | 43300.7549 | 1:40 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | SERVICE LINE DAMAGED DUE TO FIRE ON POLE | DAMAGED SERVICE LINE REPLACED | BLOCK J-NABI KARIM | 481
13 | 20.07.2018 | PHG | 43301.0091 | 43301.064 | 1:19 | HT SYSTEM FAULT | TRIPPING | BUS BAR DAMAGED SAME ATTENDED | ARAAM BAGH PAHARGANJ | 863
14 | 19.07.2018 | SRD | 43300.4806 | 43300.5236 | 1:02 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK 10-OLD RAJENDRA NAGAR | 721
15 | 19.07.2018 | YVR | 43300.4375 | 43300.5675 | 3:07 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | SUBHASH PARK-GORAKH PARK | 850 | PREVENTIVE MAINTENANCE CARRIED OUT UNDER PLANNED SHUTDOWN
16 | 19.07.2018 | YVR | 43300.6511 | 43300.7121 | 1:28 | HT SYSTEM FAULT | PLINTH OF PANEL DAMAGED | PLINTH OF PANEL REPAIRED | NAYAGAON-NEW KATWARA | 837