## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 21.07.2018 TO 06:00 HRS OF 22.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 21.07.2018 | CCK | 43302.3819 | 43302.493 | 2:40 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | FATEHPURI MASJID-CHANDNI CHOWK. | 402 | PREVENTIVE MAINTENANCE CARRIED OUT UNDER PLANNED SHUTDOWN
2 | 21.07.2018 | DGN | 43302.3496 | 43302.9821 | 15:11 | DAMAGE BY OTHER AGENCIES | 6 NO. OF LT POLE DAMAGED BY UNKNOWN VEHICLE | DAMAGED POLES AND WIRE REPAIRED | B BLOCK JHILMIL IND AREA. | 48 | 6 NO. OF LT POLE & CABLES DAMAGED BY UNKNOWN VEHICLE, SAME REPAIRED,DELAY DUE TO HEAVY RAIN
3 | 21.07.2018 | DGN | 43302.5139 | 43302.5764 | 1:30 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | POLE BROKEN DUE TO HEAVY RAIN | BROKEN POLE REPAIRED | RAM NAGAR-SEELAMPUR,DILSHAD GARDEN. | 92
4 | 21.07.2018 | DRG | 43302.6466 | 43302.7396 | 2:14 | HT SYSTEM FAULT | TRIPPING | LOOP CABLE BURNT, SAME REPAIRED | FOOTOVER BRIDGE,JAMA MASJID. | 3026 | LOOP CABLE BURNT, SAME REPAIRED
5 | 22.07.2018 | KRN | 43303.2264 | 43303.2689 | 1:01 | HT SYSTEM FAULT | TRIPPING | TRANSFORMER DD FUSE BLOWN, SAME REPLACED | RAGHUBARPURA NO 2-SEELAMPUR,KRISHNA NAGAR. | 314
6 | 21.07.2018 | KWN | 43302.4534 | 43302.5163 | 1:31 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE DAMAGED DUE TO FLASH, SAME REPAIRED | NON COMM AREA-SONIA VIHAR. | 1063
7 | 21.07.2018 | KWN | 43302.5417 | 43302.6181 | 1:50 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF DUE TO HEAVY RAIN & WATER LOGGING | WATER LOGGING AT SUB STATION, SAME REMOVED | BLOCK R-PATEL VIHAR,BLOCK CN-MANGALAM VIHAR. | 604
8 | 21.07.2018 | KWN | 43302.5424 | 43302.6181 | 1:49 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF DUE TO HEAVY RAIN & WATER LOGGING | WATER LOGGING AT SUB STATION, SAME REMOVED | PKT B-BLOCK B,BLOCK A-KARAWAL NAGAR (DEHROTI). | 861
9 | 21.07.2018 | KWN | 43302.5431 | 43302.6261 | 2:00 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF DUE TO HEAVY RAIN & WATER LOGGING | WATER LOGGING AT SUB STATION, SAME REMOVED | BLOCK E-INDIRA VIHAR,BHAGAT NAGAR-DAYALPUR. | 777
10 | 21.07.2018 | KWN | 43302.5437 | 43302.6236 | 1:55 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF DUE TO HEAVY RAIN & WATER LOGGING | WATER LOGGING AT SUB STATION, SAME REMOVED | BLOCK M-SHIV VIHAR,PKT C-BLOCK B. | 3400
11 | 21.07.2018 | KWN | 43302.5465 | 43302.6281 | 1:57 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF DUE TO HEAVY RAIN & WATER LOGGING | WATER LOGGING AT SUB STATION, SAME REMOVED | PHASE I-SHIV VIHAR,BLOCK F & G-BHAGAT SINGH COLONY. | 1939
12 | 21.07.2018 | KWN | 43302.5472 | 43302.609 | 1:29 | HVDS TRANSFORMER | TO ATTEND FAULT IN THE LINE | HVDS TRANSFORMER DD FUSE BLOWN, SAME REPLACED | CLOCK C-BIHARIPUR,BLOCK C-SHERPUR. | 355
13 | 21.07.2018 | KWN | 43302.5729 | 43302.625 | 1:15 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF DUE TO HEAVY RAIN & WATER LOGGING | WATER LOGGING AT SUB STATION, SAME REMOVED | ARVIND NAGAR-GHONDA,BLOCK H-GHONDA PATTI. | 5973
14 | 21.07.2018 | KWN | 43302.5729 | 43302.6299 | 1:22 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF DUE TO HEAVY RAIN & WATER LOGGING | WATER LOGGING AT SUB STATION, SAME REMOVED | PKT W-BLOCK A,PKT D-SHIV VIHAR,BLOCK A-HARIJAN BASTI. | 770
15 | 21.07.2018 | KWN | 43302.6601 | 43302.7176 | 1:23 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD BURNT, SAME REPAIRED | BHAGAT NAGAR-DAYALPUR,BHAJANPURA. | 1178
16 | 22.07.2018 | KWN | 43303.0132 | 43303.2222 | 5:01 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | PANAL FLASHED & HT CABLE FAULTY, AREA BACKFEEDED | SHERPUR CHOWK & BIHARIPUR VILLAGE. | 928 | PANAL FOUND FLASHED & HT CABLE FAULTY, AREA BACKFEEDED,DELAY DUE TO WATER LOGGING
17 | 22.07.2018 | KWN | 43303.2181 | 43303.3347 | 2:48 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | HVDS LEAD FOUND BURNT, SAME REPAIRED | JOHRI ENCLAVE-BHAGIRATHI VIHAR. | 1973 | HVDS LEAD FOUND BURNT, SAME REPAIRED DELAY DUE TO SPACE CONSTRAINTS & WATER LOGGING
18 | 21.07.2018 | VSE | 43302.4885 | 43302.5453 | 1:22 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD BURNT, SAME REPAIRED | MAYUR VIHAR PHASE III,BLOCK B. | 1791
19 | 21.07.2018 | VSE | 43302.9389 | 43303.2632 | 7:47 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | LTAB BURNT DUE TO FIRE ON FEEDER PILLAR | BURNT LTAB REPLACED & FEEDER PILLAR REPAIRED | BLOCK B-NEW ASHOK NAGAR VSE,BLOCK C1. | 324 | LTAB BURNT DUE TO FIRE ON FEEDER PILLAR, IT TOOK TIME TO REPLACE ONE BY ONE,DELAY DUE TO WATER LOGGING
20 | 21.07.2018 | YVR | 43302.4271 | 43302.5931 | 3:59 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | HOT SPOTS & CLEANING WORK CARRIED OUT | BLOCK C9-YAMUNA VIHAR. | 355 | PREVENTIVE MAINTENANCE CARRIED OUT UNDER PLANNED SHUTDOWN
21 | 21.07.2018 | YVR | 43302.5826 | 43302.7338 | 3:38 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | FOUND OIL LEAKAGE IN TRANSFORMER & ALSO BUSHING DAMAGED, SAME REPAIRED & HT CABLE ALSO FAULTY,AREA BACKFEEDED | BLOCK Q-BRAHM PURI,BLOCK N-BRAHM PURI. | 1381 | FOUND OIL LEAKAGE IN TRANSFORMER & ALSO BUSHING DAMAGED, SAME REPAIRED & HT CABLE ALSO FAULTY,AREA BACKFEEDED,DELAY DUE TO WATER LOGGING