## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 23.07.2018 TO 06:00 HRS OF 24.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 24.07.2018 | CCK | 43304.466 | 43304.5808 | 2:45 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | HAUZ QAZI ROAD-PEEPAL MAHADEV GALI | 1516 | PREVENTIVE MAINTENANCE WAS CARRIED OUT AT S/STN P.S.HAUZ QUAZI UNDER PLANNED SHUTDWON
2 | 24.07.2018 | DGN | 43304.3452 | 43304.4097 | 1:33 | HT SYSTEM FAULT | TRIPPING | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | JHILMIL INDUSTRIAL AREA-JHILMIL COLONY | 102
3 | 24.07.2018 | JLM | 43304.5242 | 43304.5821 | 1:23 | LT FEEDER | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | AGCR ENCLAVE-ANAND VIHAR | 60
4 | 24.07.2018 | JLM | 43304.9431 | 43304.9944 | 1:14 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | B-BLOCK JHILMILL | 467
5 | 24.07.2018 | JLM | 43304.9507 | 43305.0424 | 2:12 | HT SYSTEM FAULT | TRIPPING | HT CONSUMER'S TRANSFORMER FAULTY | CROSS RIVER MALL | 258 | BREAKDOWN OCCURRED DUE TO HT CONSUMER CROSSRIVER MALL TRANSFORMER GET FAULTY
6 | 24.07.2018 | KRN | 43304.2444 | 43304.5208 | 6:38 | DISTRIBUTION TR. | FAULT IN TRANSFORMER | FAULTY TRANSFORMER REPLACED | G BLOCK JAGATPURI | 2770 | DISTRIBUTION TRANSFORMER GOT FAULTY AT B BLK JAGATPURI DUE TO OVERLOADING AND HAVING SPACE CONSTRAINT
7 | 24.07.2018 | KWN | 43304.3617 | 43304.4201 | 1:24 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE CIRCUIT | HVDS CABLE END BOX FAULTY SAME REPAIRED | BLOCK B-SHANTI NAGAR | 129
8 | 24.07.2018 | LNR | 43304.5764 | 43304.7323 | 3:45 | DAMAGE BY OTHER AGENCIES | POLE DAMAGED BY MCD DURING DEMOLITION WORK | DAMAGED POLE REPLACED | GYAN KUNJ-WEST GURU ANGAD NAGAR | 1793 | POLE DAMAGED BY MCD DURING DEMOLITION WORK AT KULDEEP NURSING HOME S/STN
9 | 24.07.2018 | PHG | 43304.4229 | 43304.4991 | 1:50 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CHUNA MANDI-PAHAR GANJ | 259
10 | 24.07.2018 | PHG | 43304.5336 | 43304.5899 | 1:21 | DAMAGE BY OTHER AGENCIES | SUPPLY SWITCHED OFF FOR SAFETY PURPOSE ON REQUEST OF MCD | AREA NORMALISED AFTER GETTING CLEARANCE FROM MCD | CLOTH MARKET SADAR | 629
11 | 24.07.2018 | YVR | 43304.4354 | 43304.5098 | 1:47 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK R-BRAHM PURI | 1095
12 | 24.07.2018 | YVR | 43304.4481 | 43304.524 | 1:49 | LT FEEDER | NETWORK UPGRADATION | NEW LTAB CABLE LAID | LIG/MIG DDA FLATS-SHASTRI PARK | 87

## Sheet2
SR. NO. | DIVISION | SUBDIVISION | BREAKDOWN ID | FAULT ID | GRID | FEEDER | LOSS CATEGORY | SUBDIVISION LOSSES | SUBSTATION | DT | VOLTAGE | LT FEEDER | OPEN TIME | BACKFEEDED | BACKFEED TIME | AFF DURATION | BACKFEED SOURCE | STATUS | CLOSE TIME | DURATION | SCADA TIME | SCADA DUR | CLOSING STATUS | ENTRY MODE | RELAY | RELAY REASON | LOAD | ELEMENT | PROBLEM | GDR ENTRY | FAULT LOCATION | FPI INSTALLED | FPI OPERATED | REMARKS | SCADA CLOSING REMARKS | FORCE MAJEURE ELEMENT | FORCE MAJEURE SUBELEMENT | FORCE MAJEURE REASON1 | FORCE MAJEURE REASON2 | FORCE MAJEURE REASON3 | FORCE MAJEURE REASON4 | FORCE MAJEURE REMARKS | SWITCH ID | TOTAL CONSUMER AFFECTED | CLOSING REMARKS | VEHICLE ID | VEHICLE NO | VEHICLE ASSIGN TIME | VEHICLE MOVEMENT TIME | INFO BY | AREA | IMAGES | ACTION REQUIRED | ACTION TAKEN | REVIEW REASON | REVIEW REMARKS
1 | KWN | GOKUL PURI | B22071800034 | KWN22071800064 | BHAGIRATHI (66/33/11kV) GRID SSTN | (014618)->BHAGIRATHI_11kV_CB_JAGDAMBA COLONY (ALSTOM, VCB) | - | 12.1% |  |  | HT |  | 2018-07-22 11:56 | NO |  |  |  | CLOSED | 2018-07-22 12:55 | 0:58 | 2018-07-22 12:47 | 0:50 | FULLY | AUTO TRIP | AUTO TRIP | TRIPPING | 0 | TRANSIENT FAULT, | TRANSIENT FAULT, | NO VISIBLE FAULT FOUND IN AREA, TRANSIENT FAULT | NO VISIBLE FAULT FOUND IN AREA, TRANSIENT FAULT |  |  |  | FPI operated ,relay reset try at no load held ok | [7 empty] | 14618 | 7085 |  | KWN-BH-1 | DL1YE6815 | 2018-07-22 12:04 |  | SCADA | JOHRI ENCLAVE-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,BLOCK A-CHAMAN PARK,JAGDAMBA COLONY-BHAGIRATHI VIHAR,LAXMI GARDEN-AMBEDKAR NAGAR,BLOCK B-JOHRI PUR,BHAGIRATHI VIHAR,BLOCK B-JOHRI PUR,JOHRI ENCLAVE-BHAGIRATHI VIHAR,BLOCK B-CHAMAN PARK,AMBEDKAR NAGAR INDUSTRIAL AREA-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,BLOCK A-JOHRI PUR,BLOCK F-INDIRA VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHARAT-AMBEDKAR NAGAR,BHAGIRATHI VIHAR,BLOCK P-SHIV VIHAR,BLOCK F-SHIV VIHAR,SHIV VIHAR,BLOCK C-KARAWAL NAGAR,LIG/MIG RES/NON COMM AREA-SONIA VIHAR, |  | NA | NA | NA | NA
2 | KWN | GOKUL PURI | B22071800032 | KWN22071800062 | KARAWAL NAGAR 33/11kV GRID SSTN | (012126)->KARAWAL NAGAR_11 kV_CB_JHORIPUR MCD SCHOOL(ABB,VCB) | B | 12.1% |  |  | HT |  | 2018-07-22 11:34 | NO |  |  |  | CLOSED | 2018-07-22 12:27 | 0:52 | 2018-07-22 11:58 | 0:23 | PARTIAL | AUTO TRIP | AUTO TRIP | TRIPPING | 0 |  |  | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE |  |  | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE | FPI operated ,relay reset try at no load held ok | [7 empty] | 12126 | 2623 | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE | KWN-BH-1 | DL1YE6815 | 2018-07-22 11:55 |  | SCADA | BLOCK 5-GEETA COLONY,GEETA COLONY,BLOCK 7-GEETA COLONY,JOHRI ENCLAVE-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,LAXMI GARDEN-AMBEDKAR NAGAR,BLOCK B-JOHRI PUR,BHAGIRATHI VIHAR,BLOCK B-JOHRI PUR,BLOCK B-CHAMAN PARK,AMBEDKAR NAGAR INDUSTRIAL AREA-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,BLOCK A-JOHRI PUR,BLOCK F-INDIRA VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHARAT-AMBEDKAR NAGAR,BHAGIRATHI VIHAR,SHIV VIHAR, |  | NA | NA | NA | NA
3 | KWN | SONIA VIHAR | B22071800018 | KWN22071800043 | SONIA VIHAR 66/11kV GRID | (013267)->SONIA VIHAR GRID_11kV_CB_KHAJURI KHADDA | A | 13.57% |  |  | HT |  | 2018-07-22 09:45 | NO |  |  |  | CLOSED | 2018-07-22 10:45 | 0:59 | 2018-07-22 10:45 | 0:59 | FULLY | AUTO TRIP | AUTO TRIP | TRIPPING | 132 | TRANSIENT FAULT, | TRANSIENT FAULT, | FLASH IN RMU AT KHAJURI KHADDA, CLEANED PROPERLY AND FEEDER ENERGISED, BREAKDOWN APP NOT WORKING AT SITE | FLASH IN RMU AT KHAJURI KHADDA, CLEANED PROPERLY AND FEEDER ENERGISED, BREAKDOWN APP NOT WORKING AT SITE |  |  | FLASH IN RMU AT KHAJURI KHADDA, CLEANED PROPERLY AND FEEDER ENERGISED, BREAKDOWN APP NOT WORKING AT SITE | Self Permit | [7 empty] | 13267 | 5800 |  | KWN-BH-1 | DL1YE6815 | 2018-07-22 09:57 |  | SCADA | BALI MARAN-BARA DARI,BLOCK A & B-VASUNDHARA ENCLAVE,GURU ANGAD NAGAR EAST-SWASTHYA VIHAR,BLOCK F-KHAJURI KHAS EXTN.,BLOCK I-KHAJURI KHAS EXTN.,BLOCK C-KHAJURI KHAS,BLOCK C-SHERPUR,BLOCK J-KHAJURI KHAS,CLOCK C-BIHARIPUR,BLOCK A-KHAJURI KHAS,BLOCK B-KHAJURI KHAS,BLOCK C-KHAJURI KHAS,PKT A-BLOCK B,LIG/MIG RES/NON COMM AREA-BLOCK B,FATEHPURI-KUCHA HASIRAM,DARIBA KALA-KATRA MASHRU,BLOCK A-DALLU PURA VSE,DANIK JANYOG-VASUNDHARA ENCLAVE VSE, |  | NA | NA | NA | NA
4 | KWN | GOKUL PURI | B22071800003 | KWN22071800007 | BHAGIRATHI (66/33/11kV) GRID SSTN | (008281)->BHAGIRATHI_11kV_CB_BRIJPURI ROAD+LOCAL TRF-2(ALSTOM, VCB) | A | 12.1% |  |  | HT |  | 2018-07-22 05:14 | NO |  |  |  | CLOSED | 2018-07-22 05:41 | 0:26 | 2018-07-22 05:31 | 0:16 | PARTIAL | AUTO TRIP | AUTO TRIP | TRIPPING | 90 |  |  | dd fuse blown at ziauddinpur dp | DD FUSE BLOWN AT ZIAUDDINPUR DP |  |  |  | FPI operated ,relay reset try at no load held ok | [7 empty] | 8281 | 5991 |  | KWN-BH-1 | DL1YE6815 | 2018-07-22 05:41 |  | SCADA | GEETA COLONY,BLOCK E-BHAGIRATHI VIHAR,BLOCK F-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,JOHRI ENCLAVE-BHAGIRATHI VIHAR,BLOCK D-BHAGIRATHI VIHAR,BLOCK A-MAN SINGH NAGAR,BLOCK H-OLD MUSTAFABAD,BLOCK C-MAN SINGH NAGAR,BHAJANPURA-DAYALPUR,BLOCK E-BRIJ PURI,PKT R-BLOCK D,BLOCK E-INDIRA VIHAR,BLOCK C-BHAGIRATHI VIHAR,BLOCK B-MAN SINGH NAGAR,BHAGIRATHI VIHAR,BLOCK H-BHAGIRATHI VIHAR,BLOCK B-OLD MUSTAFABAD,BLOCK G-BHAGIRATHI VIHAR,BLOCK T-OLD MUSTAFABAD,BLOCK C-BRIJ PURI,BLOCK B-BHAGIRATHI VIHAR,JHILMIL INDUSTRIAL AREA-JHILMIL COLONY,GGS INDRAPRASTHA UNIVERSITY-KASHMERE GATE,BLOCK N-SHIV VIHAR,BLOCK M-SHIV VIHAR,BLOCK A-SADATPUR EXT-PUSTA AREA-L BLOCK,BLOCK F-SHIV VIHAR,PKT A-BLOCK B,LIG/MIG RES/NON COMM AREA-SONIA VIHAR,LIG/MIG RES/NON COMM AREA-SONIA VIHAR,BLOCK C-MUSTAFABAD (DAYALPUR),LIG/MIG RES/NON COMM AREA-SONIA VIHAR, |  | NA | NA | NA | NA
5 | KWN | SONIA VIHAR | B22071800001 | KWN22071800003 | SONIA VIHAR 66/11kV GRID | (026954)->SONIA VIHAR GRID_11kV_CB_SHERPUR CHOWK | - | 13.57% |  |  | HT |  | 2018-07-22 00:19 | NO |  |  |  | CLOSED | 2018-07-22 05:20 | 5:01 | 2018-07-22 00:11 | 0:-8 | FULLY | MANUAL | AUTO TRIP | TRIPPING | 80 | 11KV CABLE, | CABLE FAULT, | ht cable fualty from sherpur chowk to jile singh ki kothi and breaker bypass at sherpur chowk | HT CABLE FUALTY FROM SHERPUR CHOWK TO JILE SINGH KI KOTHI AND BREAKER BYPASS AT SHERPUR CHOWK |  |  |  | FPI operated ,relay reset try at no load held ok | CABLE DAMAGE | [6 empty] | 26954 | 928 | inform to flc | KWN-BH-1 | DL1YE6815 | 2018-07-22 00:37 |  | so | BLOCK E-BRIJ PURI,BLOCK C-BRIJ PURI,BIHARI COLONY-SHAHDARA,BLOCK C-TUKMIRPUR,BLOCK C-KHAJURI KHAS,BLOCK C-SHERPUR,CLOCK C-BIHARIPUR,BLOCK D-TUKMIRPUR,BLOCK B-KHAJURI KHAS,BLOCK B-NEHRU VIHAR,BLOCK D-SHERPUR,BLOCK D-KHAJURI KHAS,BLOCK B-CHANDU NAGAR, |  | NA | NA | NA | N