## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00 HRS. OF 25.07.2018 TO 06:00 HRS OF 26.07.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 25.07.2018 | DGN | 43306.4101 | 43306.4583 | 1:09 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | SHAMBHU NATH COMPOUND SHAHDRA | 70
2 | 25.07.2018 | DRG | 43306.4514 | 43306.5184 | 1:36 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | KUCHA PATI RAM-CHANDNI CHOWK | 1637
3 | 26.07.2018 | DRG | 43307.1425 | 43307.1996 | 1:22 | HT SYSTEM FAULT | TRIPPING | CONSUMER HT PANEL FLASHED SAME ATTENDED | PART OF I G STADIUM | 135
4 | 25.07.2018 | JLM | 43306.5757 | 43306.675 | 2:23 | LT FEEDER | LT POLE DAMAGED | DAMAGED LT POLE REPLACED | BLOCK D-ANAND VIHAR | 157 | LT POLE DAMAGED BY UNKNOWN VEHICLE SAME REPLACED
5 | 25.07.2018 | KRN | 43306.5188 | 43306.566 | 1:08 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE CIRCUIT | DP FUSE BLOWN SAME REPLACED | NEW GOVIND PURA-JAGATPURI | 258
6 | 25.07.2018 | KWN | 43306.7629 | 43306.8646 | 2:26 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | BLOCK C-MAHALAXMI ENCLAVE | 604 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
7 | 25.07.2018 | KWN | 43306.7633 | 43306.8681 | 2:31 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | BLOCK CN-MANGALAM VIHAR | 431 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
8 | 25.07.2018 | KWN | 43306.7637 | 43306.8708 | 2:34 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | BLOCK M-SHIV VIHAR | 3400 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
9 | 25.07.2018 | KWN | 43306.7641 | 43306.875 | 2:40 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | PHASE 6-SHIV VIHAR | 610 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
10 | 25.07.2018 | KWN | 43306.7739 | 43306.875 | 2:26 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | KAMAL VIHAR-KARAWAL NAGAR | 1939 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
11 | 25.07.2018 | KWN | 43306.7768 | 43306.8792 | 2:27 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | GOVIND VIHAR | 10521 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
12 | 25.07.2018 | KWN | 43306.7773 | 43306.8806 | 2:29 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | ARVIND NAGAR-GHONDA | 4613 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
13 | 25.07.2018 | KWN | 43306.7826 | 43306.8799 | 2:20 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | BLOCK F-BHAGAT SINGH COLONY | 690 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
14 | 25.07.2018 | KWN | 43306.7882 | 43306.8785 | 2:10 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | SUPPLY PUT OFF FOR SAFETY DUE TO HEAVY RAIN AND WATER LOGGING | SUPPLY NORMALISED AFTER CLEANING THE S/STN. | BHAJANPURA-DAYALPUR | 861 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
15 | 25.07.2018 | KWN | 43306.9271 | 43307.0756 | 3:34 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BEAKDOWN DUE TO HEAVY RAIN AND WATER LOGGING | HVDS LEAD FAULTY SAME REPAIRED | BLOCK D-PREM VIHAR | 1857 | SUPPLY PUT OFF FOR SAFETY PURPOSE DUE TO HEAVY RAIN AND WATER LOGGING AT S/STN.
16 | 25.07.2018 | KWN | 43306.9306 | 43306.9889 | 1:24 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE CIRCUIT | HVDS LEAD FAULTY SAME REPAIRED | GALI NO-11 C BLOCK WEST KARAWAL NAGAR | 1601
17 | 25.07.2018 | KWN | 43306.9429 | 43307.006 | 1:31 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE CIRCUIT | HVDS SOCKET DAMAGED SAME REPLACED | BLOCK D-PREM VIHAR | 3071
18 | 25.07.2018 | LNR | 43306.7542 | 43306.8146 | 1:27 | HT SYSTEM FAULT | TRIPPING | BUSBAR FLASHED SAME ATTENDED | B BLOCK LAXMI NAGAR | 860
19 | 25.07.2018 | PNR | 43306.559 | 43306.6245 | 1:34 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | DMS COLONY WEST PATEL NAGAR | 2942
20 | 25.07.2018 | PNR | 43306.6848 | 43306.7596 | 1:48 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | 18 BLOCK WEST PATEL NAGAR | 9250
21 | 25.07.2018 | VSE | 43306.7211 | 43306.8083 | 2:06 | LT FEEDER | FEEDER PILLAR DAMAGED | DAMAGED FEEDER PILLAR REPLACED | BLOCK B-NEW ASHOK NAGAR VSE | 940 | FEEDER PILLAR DAMAGED SAME REPLACED
22 | 26.07.2018 | VSE | 43307.0594 | 43307.1348 | 1:49 | LT FEEDER | TO ATTEND FAULT IN THE CIRCUIT | FIRE IN LTAB SAME REPAIRED | BLOCK A-NEW ASHOK NAGAR | 72
23 | 25.07.2018 | YVR | 43306.4715 | 43306.6299 | 3:48 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK E-ZERO PUSTA | 1778 | PREVENTIVE MAINTENANCE CARRIED OUT UNDER PLANNED SHUTDOWN
24 | 25.07.2018 | YVR | 43306.5736 | 43306.6306 | 1:22 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK F-ZERO PUSTA | 1593

## Sheet2
SR. NO. | DIVISION | SUBDIVISION | BREAKDOWN ID | FAULT ID | GRID | FEEDER | LOSS CATEGORY | SUBDIVISION LOSSES | SUBSTATION | DT | VOLTAGE | LT FEEDER | OPEN TIME | BACKFEEDED | BACKFEED TIME | AFF DURATION | BACKFEED SOURCE | STATUS | CLOSE TIME | DURATION | SCADA TIME | SCADA DUR | CLOSING STATUS | ENTRY MODE | RELAY | RELAY REASON | LOAD | ELEMENT | PROBLEM | GDR ENTRY | FAULT LOCATION | FPI INSTALLED | FPI OPERATED | REMARKS | SCADA CLOSING REMARKS | FORCE MAJEURE ELEMENT | FORCE MAJEURE SUBELEMENT | FORCE MAJEURE REASON1 | FORCE MAJEURE REASON2 | FORCE MAJEURE REASON3 | FORCE MAJEURE REASON4 | FORCE MAJEURE REMARKS | SWITCH ID | TOTAL CONSUMER AFFECTED | CLOSING REMARKS | VEHICLE ID | VEHICLE NO | VEHICLE ASSIGN TIME | VEHICLE MOVEMENT TIME | INFO BY | AREA | IMAGES | ACTION REQUIRED | ACTION TAKEN | REVIEW REASON | REVIEW REMARKS
1 | KWN | GOKUL PURI | B22071800034 | KWN22071800064 | BHAGIRATHI (66/33/11kV) GRID SSTN | (014618)->BHAGIRATHI_11kV_CB_JAGDAMBA COLONY (ALSTOM, VCB) | - | 12.1% |  |  | HT |  | 2018-07-22 11:56 | NO |  |  |  | CLOSED | 2018-07-22 12:55 | 0:58 | 2018-07-22 12:47 | 0:50 | FULLY | AUTO TRIP | AUTO TRIP | TRIPPING | 0 | TRANSIENT FAULT, | TRANSIENT FAULT, | NO VISIBLE FAULT FOUND IN AREA, TRANSIENT FAULT | NO VISIBLE FAULT FOUND IN AREA, TRANSIENT FAULT |  |  |  | FPI operated ,relay reset try at no load held ok | [7 empty] | 14618 | 7085 |  | KWN-BH-1 | DL1YE6815 | 2018-07-22 12:04 |  | SCADA | JOHRI ENCLAVE-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,BLOCK A-CHAMAN PARK,JAGDAMBA COLONY-BHAGIRATHI VIHAR,LAXMI GARDEN-AMBEDKAR NAGAR,BLOCK B-JOHRI PUR,BHAGIRATHI VIHAR,BLOCK B-JOHRI PUR,JOHRI ENCLAVE-BHAGIRATHI VIHAR,BLOCK B-CHAMAN PARK,AMBEDKAR NAGAR INDUSTRIAL AREA-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,BLOCK A-JOHRI PUR,BLOCK F-INDIRA VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHARAT-AMBEDKAR NAGAR,BHAGIRATHI VIHAR,BLOCK P-SHIV VIHAR,BLOCK F-SHIV VIHAR,SHIV VIHAR,BLOCK C-KARAWAL NAGAR,LIG/MIG RES/NON COMM AREA-SONIA VIHAR, |  | NA | NA | NA | NA
2 | KWN | GOKUL PURI | B22071800032 | KWN22071800062 | KARAWAL NAGAR 33/11kV GRID SSTN | (012126)->KARAWAL NAGAR_11 kV_CB_JHORIPUR MCD SCHOOL(ABB,VCB) | B | 12.1% |  |  | HT |  | 2018-07-22 11:34 | NO |  |  |  | CLOSED | 2018-07-22 12:27 | 0:52 | 2018-07-22 11:58 | 0:23 | PARTIAL | AUTO TRIP | AUTO TRIP | TRIPPING | 0 |  |  | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE |  |  | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE | FPI operated ,relay reset try at no load held ok | [7 empty] | 12126 | 2623 | HT CABLE AT JOHRIPUR SCHOOL S/STN DOUBTFUL, ALL OTHER AREA ENERGISED, MOBILE APP NOT WORKING AT SITE | KWN-BH-1 | DL1YE6815 | 2018-07-22 11:55 |  | SCADA | BLOCK 5-GEETA COLONY,GEETA COLONY,BLOCK 7-GEETA COLONY,JOHRI ENCLAVE-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,LAXMI GARDEN-AMBEDKAR NAGAR,BLOCK B-JOHRI PUR,BHAGIRATHI VIHAR,BLOCK B-JOHRI PUR,BLOCK B-CHAMAN PARK,AMBEDKAR NAGAR INDUSTRIAL AREA-BHAGIRATHI VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,BLOCK A-JOHRI PUR,BLOCK F-INDIRA VIHAR,TUNDA NAGAR-BHAGIRATHI VIHAR,BHARAT-AMBEDKAR NAGAR,BHAGIRATHI VIHAR,SHIV VIHAR, |  | NA | NA | NA | NA
3 | KWN | SONIA VIHAR | B22071800018 | KWN22071800043 | SONIA VIHAR 66/11kV GRID | (013267)->SONIA VIHAR GRID_11kV_CB_KHAJURI KHADDA | A | 13.57% |  |  | HT |  | 2018-07-22 09:45 | NO |  |  |  | CLOSED | 2018-07-22 10:45 | 0:59 | 2018-07-22 10:45 | 0:59 | FULLY | AUTO TRIP | AUTO TRIP | TRIPPING | 132 | TRANSIENT FAULT, | TRANSIENT FAULT, | FLASH IN RMU AT KHAJURI KHADDA, CLEANED PROPERLY AND FEEDER ENERGISED, BREAKDOWN APP NOT WORKING AT SITE | FLASH IN RMU AT KHAJURI KHADDA, CLEANED PROPERLY AND FEEDER ENERGISED, BREAKDOWN APP NOT WORKING AT SITE |  |  | FLASH IN RMU AT KHAJURI KHADDA, CLEANED PROPERLY AND FEEDER ENERGISED, BREAKDOWN APP NOT WORKING AT SITE | Self Permit | [7 empty] | 13267 | 5800 |  | KWN-BH-1 | DL1YE6815 | 2018-07-22 09:57 |  | SCADA | BALI MARAN-BARA DARI,BLOCK A & B-VASUNDHARA ENCLAVE,GURU ANGAD NAGAR EAST-SWASTHYA VIHAR,BLOCK F-KHAJURI KHAS EXTN.,BLOCK I-KHAJURI KHAS EXTN.,BLOCK C-KHAJURI KHAS,BLOCK C-SHERPUR,BLOCK J-KHAJURI KHAS,CLOCK C-BIHARIPUR,BLOCK A-KHAJURI KHAS,BLOCK B-KHAJURI KHAS,BLOCK C-KHAJURI KHAS,PKT A-BLOCK B,LIG/MIG RES/NON COMM AREA-BLOCK B,FATEHPURI-KUCHA HASIRAM,DARIBA KALA-KATRA MASHRU,BLOCK A-DALLU PURA VSE,DANIK JANYOG-VASUNDHARA ENCLAVE VSE, |  | NA | NA | NA | NA
4 | KWN | GOKUL PURI | B22071800003 | KWN22071800007 | BHAGIRATHI (66/33/11kV) GRID SSTN | (008281)->BHAGIRATHI_11kV_CB_BRIJPURI ROAD+LOCAL TRF-2(ALSTOM, VCB) | A | 12.1% |  |  | HT |  | 2018-07-22 05:14 | NO |  |  |  | CLOSED | 2018-07-22 05:41 | 0:26 | 2018-07-22 05:31 | 0:16 | PARTIAL | AUTO TRIP | AUTO TRIP | TRIPPING | 90 |  |  | dd fuse blown at ziauddinpur dp | DD FUSE BLOWN AT ZIAUDDINPUR DP |  |  |  | FPI operated ,relay reset try at no load held ok | [7 empty] | 8281 | 5991 |  | KWN-BH-1 | DL1YE6815 | 2018-07-22 05:41 |  | SCADA | GEETA COLONY,BLOCK E-BHAGIRATHI VIHAR,BLOCK F-BHAGIRATHI VIHAR,BHAGIRATHI VIHAR,JOHRI ENCLAVE-BHAGIRATHI VIHAR,BLOCK D-BHAGIRATHI VIHAR,BLOCK A-MAN SINGH NAGAR,BLOCK H-OLD MUSTAFABAD,BLOCK C-MAN SINGH NAGAR,BHAJANPURA-DAYALPUR,BLOCK E-BRIJ PURI,PKT R-BLOCK D,BLOCK E-INDIRA VIHAR,BLOCK C-BHAGIRATHI VIHAR,BLOCK B-MAN SINGH NAGAR,BHAGIRATHI VIHAR,BLOCK H-BHAGIRATHI VIHAR,BLOCK B-OLD MUSTAFABAD,BLOCK G-BHAGIRATHI VIHAR,BLOCK T-OLD MUSTAFABAD,BLOCK C-BRIJ PURI,BLOCK B-BHAGIRATHI VIHAR,JHILMIL INDUSTRIAL AREA-JHILMIL COLONY,GGS INDRAPRASTHA UNIVERSITY-KASHMERE GATE,BLOCK N-SHIV VIHAR,BLOCK M-SHIV VIHAR,BLOCK A-SADATPUR EXT-PUSTA AREA-L BLOCK,BLOCK F-SHIV VIHAR,PKT A-BLOCK B,LIG/MIG RES/NON COMM AREA-SONIA VIHAR,LIG/MIG RES/NON COMM AREA-SONIA VIHAR,BLOCK C-MUSTAFABAD (DAYALPUR),LIG/MIG RES/NON COMM AREA-SONIA VIHAR, |  | NA | NA | NA | NA
5 | KWN | SONIA VIHAR | B22071800001 | KWN22071800003 | SONIA VIHAR 66/11kV GRID | (026954)->SONIA VIHAR GRID_11kV_CB_SHERPUR CHOWK | - | 13.57% |  |  | HT |  | 2018-07-22 00:19 | NO |  |  |  | CLOSED | 2018-07-22 05:20 | 5:01 | 2018-07-22 00:11 | 0:-8 | FULLY | MANUAL | AUTO TRIP | TRIPPING | 80 | 11KV CABLE, | CABLE FAULT, | ht cable fualty from sherpur chowk to jile singh ki kothi and breaker bypass at sherpur chowk | HT CABLE FUALTY FROM SHERPUR CHOWK TO JILE SINGH KI KOTHI AND BREAKER BYPASS AT SHERPUR CHOWK |  |  |  | FPI operated ,relay reset try at no load held ok | CABLE DAMAGE | [6 empty] | 26954 | 928 | inform to flc | KWN-BH-1 | DL1YE6815 | 2018-07-22 00:37 |  | so | BLOCK E-BRIJ PURI,BLOCK C-BRIJ PURI,BIHARI COLONY-SHAHDARA,BLOCK C-TUKMIRPUR,BLOCK C-KHAJURI KHAS,BLOCK C-SHERPUR,CLOCK C-BIHARIPUR,BLOCK D-TUKMIRPUR,BLOCK B-KHAJURI KHAS,BLOCK B-NEHRU VIHAR,BLOCK D-SHERPUR,BLOCK D-KHAJURI KHAS,BLOCK B-CHANDU NAGAR, |  | NA | NA | NA | N