## Format
DISCOM : BRPL
OUTAGE REPORT FOR : 26/07/2018 06:00Hr. To 27/07/2018 06:00Hr.
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Area / DT Effected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Detail
1 | 26/07/2018 | VKJ | 06:01 | 07:42 | 01:40 | HT SYSTEM FAULT | Grid:66kV I.A.A.I PALAM GRID To Feeder:11 kV FDR WESTERN GREEN , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : SAMALKA,RAJOKRI, | 456
2 | 26/07/2018 | SVR | 06:20 | 07:45 | 01:25 | HT SYSTEM FAULT | Grid:JASOLA (66/33/11kV) GRID SSTN To Feeder:11kV FDR SPORTS COMPLEX JASOLA , HT O/H,:HTAB FAULTY, | RESTORED/ REPAIRED | Part of : JASOLA VILLAGE_1, SARITA VIHAR BLOCK A,SARITA VIHAR BLOCK B,SARITA VIHAR BLOCK K | 569
3 | 26/07/2018 | NGL | 06:48 | 07:52 | 01:03 | HT SYSTEM FAULT | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR UDYOG NAGAR NO.-1 , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : UDYOG NAGAR_2, | 132
4 | 26/07/2018 | MDK | 07:09 | 08:25 | 01:15 | HT SYSTEM FAULT | Grid:NANGLOI WATER WORKS (66/11kV) GRID SSTN To Feeder:11kV FDR KUNWAR SINGH NAGAR , 11KV GRID PANEL,:BUSBAR FLASH, | RESTORED/ REPAIRED | Part of : LAXMI PARK COLONY,SHAFIPUR RANHOLA VILLAGE_1,AAKASH VIHAR | 525
5 | 26/07/2018 | NJF | 07:32 | 09:26 | 01:53 | HT SYSTEM FAULT | Grid:JAFFARPUR (66/11kV) GRID SSTN To Feeder:11KV PANDWALA , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : KHARKHARI NAHAR_2,UJWA_1,SHERPUR DAIRY,KHAIRA_1,GOPAL NAGAR_1,,HANS NAGAR_1,KHARKHARI ROND_2,FARM HOUSE VASANT KUNJ_4 | 712
6 | 26/07/2018 | DWK | 07:54 | 09:18 | 01:24 | HVDS CABLE & OTHER SYSTEM | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR 210 DDA FLATS SEC-3 , HVDS,:HVDS TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : PAPAN KALAN,,BLOCK C WEST END,WEST END | 524
7 | 26/07/2018 | PLM | 08:28 | 09:58 | 01:29 | HT SYSTEM FAULT | Grid:G-6 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11kV FDR SECTOR-9, POKET-1 , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : DWARKA SEC.9 PKT1,DWARKA SECTOR 9,,DWARKA SECTOR 9 PKT 2 | 549
8 | 26/07/2018 | TGN | 09:07 | 12:59 | 03:52 | PLANNED SHUTDOWN | Grid:VISHAL (33/11kV) GRID SSTN To Feeder:11kV FDR A-BLOCK S/N TAGORE GARDEN , TRANSFORMER:REMOVAL OF MOBILE TRANSFORMER & REPLACEMENT OF NEW TRANSFORMER | RESTORED/ REPAIRED | Part of : TAGORE GARDEN EXTN BLOCK A,,VISHAL ENCLAVE,TAGORE GARDEN EXTN BLOCK EA | 456
9 | 26/07/2018 | DWK | 09:19 | 10:29 | 01:10 | HT SYSTEM FAULT | Grid:G 4 DWARKA SEC 19 GRID SSTN To Feeder:11kV FDR SEC-16C DELHI POLICE QUARTERS , HT O/H,:ELECTROCUTION OF EXTERNAL ELEMENTS, | RESTORED/ REPAIRED | Part of : DWARKA SECTOR 16C_1, | 458
10 | 26/07/2018 | MDK | 10:31 | 11:36 | 01:05 | HVDS CABLE & OTHER SYSTEM | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR RAJENDERA PARK , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : TYAGY COLONY,,RAJENDRA PARK EXTN.,NANGLOI EXTN.,RATAN BAGH_1,TIKRI KALAN VILLAGE_2 | 585
11 | 26/07/2018 | SKT | 10:40 | 11:41 | 01:00 | LT FEEDER | Grid:33 kV SHIVALIK GRID To Feeder:11 kV FDR RPS SAIKH SARAI PHASE-1 , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : SEKH SARAI PHASE I | 59
12 | 26/07/2018 | JKP | 11:07 | 15:35 | 04:28 | PLANNED SHUTDOWN | Grid:D.C. JANAKPURI (33/11kV) GRID SSTN To Feeder:11KV JYOTI SIKHAR PLOT NO.-8 (NOW RMU) , RMU:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : JANAKPURI DISTRICT CENTRE, | 345
13 | 26/07/2018 | TGN | 11:21 | 12:21 | 01:00 | HT SYSTEM FAULT | Grid:BODELLA-II GRID To Feeder:11 KV FDR MBS NAGAR , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : D.D.A COLONY,,SANT GARH,SAHPURA_1,PRITHVI PARK,GURU NANAK NAGAR | 450
14 | 26/07/2018 | RKP | 11:25 | 13:14 | 01:49 | LT FEEDER | Grid:VASANT VIHAR (33/11kV) GRID SSTN To Feeder:11kV FDR SUBROTO PARK (MES) , LT ACB,:LT ACB FLASH, | RESTORED/ REPAIRED | Part of : VILLAGE JHARERA, INDIAN AIRLINES AND AIR INDIA ESTATE, | 62
15 | 26/07/2018 | NJF | 11:48 | 13:04 | 01:16 | HT SYSTEM FAULT | Grid:DELHI JAL BOARD NAJAFGARH WATER WORKS (66/11) To Feeder:11KV FDR SHYAM VIHAR , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : SHYAM VIHAR COLONY PHASE-I BLOCK-B,,DHARAM PURA_2,DINDARPUR_1 | 527
16 | 26/07/2018 | VKJ | 12:07 | 16:42 | 04:35 | PLANNED SHUTDOWN | Grid:66kV VASANT KUNJ B-BLK GRID To Feeder:11 kV FDR S.T.P FEEDER , LT CIRCUIT:NETWORK UPGRADTION WORK | RESTORED/ REPAIRED | Part of : JAWAHARLAL NEHRU UNIVERSITY CAMPUS, | 1
17 | 26/07/2018 | DWK | 12:26 | 13:50 | 01:23 | HT SYSTEM FAULT | Grid:PAPPANKALAN-II (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR NAND VIHAR , HT O/H,:CONDUCTOR SNAPPED, | RESTORED/ REPAIRED | Part of : PATEL GARDEN,SQUARTER SETTLEMENT,,SECTOR 16A_1,HARI VIHAR_1,NAND VIHAR,TRANSIT CAMP,HARI VIHAR,SHIVANI ENCLAVE,BHARAT VIHAR,TARA NAGAR,HARI VIHAR BLOCK- C,SEC 15,NAWADA MAJRA | 665
18 | 26/07/2018 | NGL | 13:04 | 14:12 | 01:07 | HVDS CABLE & OTHER SYSTEM | Grid:NANGLOI WATER WORKS (66/11kV) GRID SSTN To Feeder:11 KV FDR SAINI MOHALLA NEAR WATER TANK , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : NIHAL VIHAR_1,NARESH PARK EXTN.,NARESH PARK EXTN. | 608
19 | 26/07/2018 | SVR | 13:27 | 15:03 | 01:36 | LT FEEDER | Grid:JAMIA MILIA (33/11kV) GRID SSTN To Feeder:11kV FDR ZAKIR NAGAR , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : ZAKIR NAGAR, | 158
20 | 26/07/2018 | KPR | 13:31 | 15:19 | 01:47 | LT FEEDER | Grid:66kV BATRA GRID To Feeder:11kV FDR S/S NO.-5 DAKSHIN PURI , LT POLE,:POLE BROKEN DUE TO STRUCK BY VEHICLE, | RESTORED/ REPAIRED | Part of : DAKSHINPURI EXTENSION_2 | 78
21 | 26/07/2018 | MDK | 13:46 | 14:58 | 01:12 | HT SYSTEM FAULT | Grid:66/11KV MUNDKA GRID To Feeder:11kV FDR P.V.C MARKET-1 , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : TIKRI KALAN VILLAGE_2, | 544
22 | 26/07/2018 | HKS | 13:59 | 15:32 | 01:33 | HT SYSTEM FAULT | Grid:BHIKAJI CAMA PLACE (33/11kV) GRID SSTN To Feeder:B-6, S.J ENCLAVE , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : BLOCK B6,AN JHA DEER PARK | 325
23 | 26/07/2018 | SKT | 14:00 | 16:10 | 02:10 | PLANNED SHUTDOWN | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR N.B.C.C , RMU:HT BUSHING REPLACEMENT | RESTORED/ REPAIRED | Part of : ANDHERIA MOR, | 455
24 | 26/07/2018 | JKP | 14:08 | 15:43 | 01:35 | HT SYSTEM FAULT | Grid:HARI NAGAR (66/11kV) GRID SSTN To Feeder:11KV GANDHI PARK , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : HARI NAGAR BLOCK M,HARI NAGAR BLOCK A,HARI NAGAR BLOCK B,HARI NAGAR BLOCK BE,DELHI MILK SCHEME COLONY,NANAK PURA,BLOCK B MAYAPURI,MAYAPURI INDUSTRIAL AREA PHASE I | 571
25 | 26/07/2018 | MNG | 14:11 | 15:27 | 01:16 | EMERGENCY SHUTDOWN | Grid:HASTAL (66/11kV) GRID SSTN To Feeder:11KV FDR JHANDA CHOWK OM VIHAR , HVDS:MAINTENANCE | RESTORED/ REPAIRED | Part of : OM VIHAR PHASE V,,NAWADA MAJRA,MOHAN GARDEN BLOCK F,MOHAN GARDEN BLOCK K,UDAY PARK | 559
26 | 26/07/2018 | RKP | 14:14 | 15:32 | 01:17 | HT SYSTEM FAULT | Grid:BHIKAJI CAMA PLACE (33/11kV) GRID SSTN To Feeder:11kV FDR PLOT NO.-16 (GAIL)B.C PLACE , HT CONSUMER,:CONSUMER HT PANEL FLASH, | RESTORED/ REPAIRED | Part of : BHIKAJI CAMA PLACE_2, | 23
27 | 26/07/2018 | MNG | 14:16 | 15:26 | 01:10 | EMERGENCY SHUTDOWN | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR NAWADA , HVDS:MAINTENANCE | RESTORED/ REPAIRED | Part of : MOHAN GARDEN BLOCK A,MANSA RAM PARK BLOCK A,MANSA RAM PARK_2 | 452
28 | 26/07/2018 | NGL | 14:48 | 15:54 | 01:05 | HT SYSTEM FAULT | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR NANGLOI NO-1 , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : SHIV VIHAR NEAR NANGLOI JAT,NIHAL VIHAR_1,JJ COLONY NO 3 | 652
29 | 26/07/2018 | VKJ | 14:57 | 16:37 | 01:39 | EMERGENCY SHUTDOWN | Grid:VASANT KUNJ (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11 KV FDR I.A.A.I COLONY_VKJ , 11KV FEEDER:PREVENTIVE MAINTENANCE | RESTORED/ REPAIRED | Part of : MILAKPUR KOHI RANGPURI,RANG PURI, | 566
30 | 26/07/2018 | HKS | 17:22 | 18:55 | 01:32 | HT SYSTEM FAULT | Grid:J.N.U. (66/33/11kV) GRID SSTN To Feeder:11kV FDR DEPTT. OF IMMUNOLOGY , HT CONSUMER,:CONSUMER HT PANEL FLASH, | RESTORED/ REPAIRED | Part of : IMUNOLOGY (HTC) | 1
31 | 26/07/2018 | TGN | 17:52 | 19:37 | 01:44 | HT SYSTEM FAULT | Grid:CHAUKHANDI (33/11kV) GRID SSTN To Feeder:11kV FDR 224-SFS QTS , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : SAHIB PURA,MAJOR BHUPENDER SINGH NAGAR,SAHPURA_1 | 488
32 | 26/07/2018 | MNG | 21:24 | 22:56 | 01:31 | LT FEEDER | Grid:DELHI JAL BOARD NAJAFGARH WATER WORKS (66/11) To Feeder:11KV FDR GANDHI CHOWK , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : BHAGWATI GARDEN EXTENSION, | 163
33 | 26/07/2018 | SVR | 22:04 | 23:41 | 01:36 | HT SYSTEM FAULT | Grid:66/11KV MEETHAPUR GRID SUB STN To Feeder:11kV FDR GYAN MANDIR , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : SAURAV VIHAR,,MOLARBAND_1 | 458
34 | 27/07/2018 | VKJ | 00:29 | 02:03 | 01:33 | LT FEEDER | Grid:66kV VASANT KUNJ D-BLK GRID To Feeder:11 kV FDR NANGAL DAIRY-2 , LT U/G CABLE,:CABLE BURNT, | RESTORED/ REPAIRED | Part of : MILAKPUR KOHI RANGPURI, | 52
35 | 27/07/2018 | KPR | 01:08 | 02:52 | 01:44 | HT SYSTEM FAULT | Grid:66kV BATRA GRID To Feeder:11kV FDR A-BLOCK RAJU PARK , 11KV GRID PANEL,:BUSBAR FLASH, | RESTORED/ REPAIRED | Part of : JAWAHAR PARK_1,,DEOLI | 584
36 | 27/07/2018 | VKJ | 01:14 | 02:36 | 01:21 | HT SYSTEM FAULT | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR SECTOR-A VASANT KUNJ , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : VASANT KUNJ SECTOR A,,PKT B & C | 477
37 | 27/07/2018 | ALN | 01:22 | 02:25 | 01:02 | HT SYSTEM FAULT | Grid:33 kV ALAKNANDA GRID To Feeder:11 kV FDR SHIVALIK APPARTMENT , 11KV GRID PANEL,:BUSBAR FLASH, | RESTORED/ REPAIRED | Part of : ALAKNANDA_1, KALKAJI BLOCK D,,KALKAJI EXTENSION_2 | 385
38 | 27/07/2018 | SKT | 01:30 | 02:33 | 01:02 | HT SYSTEM FAULT | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR SATABARI , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : SAHOARPUR VILLAGE,CHANDANHULA VILLAGE_2,SATBARI VILLAGE_1, | 519
39 | 27/07/2018 | MDK | 01:31 | 02:56 | 01:24 | HT SYSTEM FAULT | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV BAKKARWALA VILLAGE , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : RAJDHANI PARK,NANGLOI EXTN.,AMAR COLONY_2,VEENA ENCLAVE | 578
40 | 27/07/2018 | PLM | 01:43 | 03:32 | 01:49 | HT SYSTEM FAULT | Grid:SAGARPUR (66/11kV) GRID SSTN To Feeder:11kV FDR F-BLOCK SAGARPUR , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : MOHAN NAGAR,BLOCK RZ_2,SAGARPUR MAIN,SAGARPUR MAIN RZ,VASHISHT PARK_2,BLOCK WZB | 635
41 | 27/07/2018 | SVR | 02:18 | 03:59 | 01:41 | HT SYSTEM FAULT | Grid:SARAI JULLENA (33/11kV) GRID SSTN To Feeder:11kV FDR MR CHILDERN SOCITY , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : DON BASCO SCHOOL*,*MEN.RETED.CHILDREN | 2
42 | 27/07/2018 | SKT | 02:26 | 03:40 | 01:13 | HT SYSTEM FAULT | Grid:66kV C-DOT GRID To Feeder:11KV FDR N.B.C.C , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : GADAIPUR VILLAGE_2,,SULTANPUR,JONAPUR VILLAGE_1,CHANDANHULA VILLAGE_1 | 521
43 | 27/07/2018 | SKT | 02:54 | 04:24 | 01:29 | LT FEEDER | Grid:66kV MALVIYA NAGAR GRID To Feeder:11kV FDR SEC-4, S/S NO.-11 PUSHP VIHAR , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : PARYAVARAN COMPLEX,MEHRAULI BADARPUR ROAD, | 45
44 | 27/07/2018 | ALN | 03:28 | 04:46 | 01:17 | HT SYSTEM FAULT | Grid:TUGHLAKABAD (33/11kV) GRID SSTN To Feeder:11kV FDR TUGLAKABAD EXTN. O/H , 11KV CABLE,:END TERMINATION DAMAGE, | RESTORED/ REPAIRED | Part of : TUGHLAKABAD EXTENSION, | 645
45 | 27/07/2018 | RKP | 04:07 | 05:47 | 01:39 | HT SYSTEM FAULT | Grid:RIDGE VALLEY (66/33/11kV) GRID SSTN To Feeder:11kV FDR COD , HT CONSUMER,:CT MOISTURE/DAMAGED, | RESTORED/ REPAIRED | Part of : MES,B.I.LINE | 1
46 | 27/07/2018 | RKP | 04:09 | 05:49 | 01:40 | HT SYSTEM FAULT | Grid:RIDGE VALLEY (66/33/11kV) GRID SSTN To Feeder:11kV FDR ST. LTG. NO.-1 , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : SUBROTO PARK,,JHEEL PARK | 392
47 | 27/07/2018 | VKP | 04:55 | 06:21 | 01:25 | HT SYSTEM FAULT | Grid:BODELLA-II GRID To Feeder:11KV L.I.G-2 HASTSAL , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : HASTSAL,VIJAY VIHAR,,MOHAN GARDEN BLOCK K,OM VIHAR PHASE V | 724