## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 22.06.2018 TO 06:00 HRS OF 23.06.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 23.06.2018 | DGN | 43274.057 | 43274.1167 | 1:26 | LT FEEDER | TO ATTEND FAULT IN THE LINE | DP FUSE BLOWN SAME REPLACED | BLOCK A-PRATAP PURA | 175
2 | 22.06.2018 | KRN | 43273.9706 | 43274.0318 | 1:28 | LT FEEDER | SERVICE CABLE DAMAGED DUE TO FIRE ON POLE | DAMAGED SERVICE CABLE REPAIRED | RASHID MARKET-JAGATPURI | 1381
3 | 23.06.2018 | KRN | 43274.0347 | 43274.1174 | 1:59 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FIRE ON POLE | DAMAGED WIRE REPAIRED | BLOCK E-ANARKALI COLONY NORTH | 472
4 | 23.06.2018 | KRN | 43274.046 | 43274.0976 | 1:14 | LT FEEDER | SERVICE CABLE DAMAGED DUE TO FIRE ON POLE | DAMAGED SERVICE CABLE REPAIRED | BLOCK A-BALDEV PARK EAST | 235
5 | 23.06.2018 | KRN | 43274.1424 | 43274.2103 | 1:38 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT LEAD FAULTY SAME ATTENDED | POLICE STATION KRISHNA NAGAR | 480
6 | 22.06.2018 | KWN | 43273.4817 | 43273.5615 | 1:55 | LT FEEDER | TO ATTEND FAULT IN THE LINE | PRC BURNT SAME ATTENDED | BLOCK D-3 NEHRU VIHAR | 62
7 | 22.06.2018 | LNR | 43273.9841 | 43274.0347 | 1:13 | LT FEEDER | SERVICE LINE DAMAGED DUE TO FIRE IN HOUSE | SERVICE LINE REPAIRED | BLOCK E-LAKSHMI NAGAR | 1203
8 | 22.06.2018 | LNR | 43273.9854 | 43274.0417 | 1:21 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK B-SWASTHYA VIHAR | 27
9 | 22.06.2018 | MVR | 43273.9569 | 43274.0119 | 1:19 | LT FEEDER | SERVICE CABLE DAMAGED DUE TO FIRE ON POLE | DAMAGED SERVICE CABLE REPAIRED | BLOCK 24-TRILOKPURI PHASE II | 371
10 | 22.06.2018 | MVR | 43273.9644 | 43274.0116 | 1:08 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | CABLE DAMAGED DUE TO FIRE ON POLE | DAMAGED SERVICE CABLE REPAIRED | BLOCK F-PANDAV NAGAR | 341
11 | 23.06.2018 | MVR | 43274.0514 | 43274.1297 | 1:53 | LT FEEDER | TO ATTEND FAULT IN THE LINE | PRC BURNT SAME ATTENDED | AMBEDKAR AWAS KALYAN SAMITI-GHAROLI KONDLI | 325
12 | 22.06.2018 | NNG | 43273.9758 | 43274.0247 | 1:10 | LT FEEDER | TO ATTEND FAULT IN THE LINE | SOCKET BURNT SAME REPLACED | BLOCK B-KABIR NAGAR | 984
13 | 22.06.2018 | YVR | 43273.5097 | 43273.5729 | 1:31 | HT SYSTEM FAULT | LT ACB FLASHED | LTACB BY PASSED | BLOCK A-GARI MANDU | 1040
14 | 22.06.2018 | YVR | 43273.5132 | 43273.5602 | 1:08 | HT SYSTEM FAULT | TRIPPING | TRANSIENT FAULT | A-BLOCK BHAJANPURA | 639