## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 23.06.2018 TO 06:00 HRS OF 24.06.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 23.06.2018 | DRG | 43274.4233 | 43274.4777 | 1:18 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | SHANKAR GALI MINTO ROAD | 1245
2 | 23.06.2018 | JLM | 43274.5342 | 43274.7536 | 5:16 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | LT POLE DAMAGED DUE TO TREE FALLEN ON POLE | DAMAGED POLE REPLACED | PART OF D ANAND VIHAR | 397 | LT POLE DAMAGED AS TREE FALLEN ON POLE SAME REPLACED
3 | 23.06.2018 | KRN | 43274.471 | 43274.5527 | 1:58 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | AZAD NAGAR EAST | 101
4 | 23.06.2018 | KRN | 43274.7907 | 43274.9663 | 4:12 | DISTRIBUTION TR. | OIL THEFT FROM 990KVA TRANSFORMER BY UNKNOWN MISCREANTS | TRANSFORMER REPLACED | PART OF A & B BLOCK JAGATPURI | 499 | MOBILE TRANSFORMER INSTALLED
5 | 23.06.2018 | KWN | 43274.6146 | 43274.6667 | 1:15 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | SHANTI NAGAR KWR | 613
6 | 24.06.2018 | KWN | 43275.17 | 43275.25 | 1:55 | HVDS CABLE & OTHER SYSTEM | HVDS LEAD FAULTY | HVDS LEAD REPLACED | BLOCK D-WEST KARAWAL NAGAR | 125
7 | 24.06.2018 | KWN | 43275.2042 | 43275.2847 | 1:56 | HT SYSTEM FAULT | TRIPPING | HVDS DP FUSE BLOWN SAME REPLACED | PART-6 SONIA VIHAR | 750
8 | 24.06.2018 | KWN | 43275.2324 | 43275.2958 | 1:31 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | GOVIND VIHAR | 525
9 | 23.06.2018 | MVR | 43274.4885 | 43274.6327 | 3:28 | LT FEEDER | LTAB BURNT DUE TO FIRE | BURNT LTAB REPLACED | SHASHI GARDEN JAVAHAR MOHALLA | 197 | LTAB BURNT DUE TO FIRE SAME REPLACED
10 | 23.06.2018 | PNR | 43274.29 | 43274.5283 | 5:43 | LT FEEDER | LT CABLE BURNT | DAMAGED CABLE REPLACED | BLOCK 26,36,37,42 & 43-WEST PATEL NAGAR | 1014 | LT CABLE BURNT SAME REPLACED