## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 24.06.2018 TO 06:00 HRS OF 25.06.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 24.06.2018 | CCK | 43275.396 | 43275.4583 | 1:30 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT | MOBILE TRANSFORMER REPLACEMENT | MOTIA MAHAL-CHANDNI CHOWK | 776
2 | 24.06.2018 | JLM | 43275.5447 | 43275.7819 | 5:42 | LT FEEDER | POLE BROKEN | REPLACEMENT OF BROKEN POLE | BHOLA NATH NAGAR | 118 | LT POLE DAMAGED BY UNKNOWN VEHICLE.
3 | 24.06.2018 | KWN | 43275.5375 | 43275.6285 | 2:11 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACK FEEDED | D BLK DYALPUR | 10712 | 11 KV CABLE GET DAMAGED BY EXTERNAL AGENCY- DJB
4 | 24.06.2018 | LNR | 43275.5352 | 43275.6007 | 1:34 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACK FEEDED | MILAN VIHAR, INDRAPRASTHA APPT. | 1197
5 | 24.06.2018 | LNR | 43275.5403 | 43275.6306 | 2:10 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACK FEEDED | SHAKARPUR CHUNGI | 2219 | 11 KV CABLE GET DAMAGED BY EXTERNAL AGENCY- MCD
6 | 25.06.2018 | NNG | 43276.0628 | 43276.1667 | 2:30 | HT SYSTEM FAULT | TRIPPING | BACK PANEL THEFT | JAGATPURI EXT | 518 | 11 KV CABLE GET FAULTY & THEFT OF PANEL COVERS DUE TO WHICH IDENTIFICATION OF CABLE TOOK MORE TIME.
7 | 24.06.2018 | PHG | 43275.6147 | 43275.6667 | 1:15 | DISTRIBUTION TR. | OIL LEAKAGE IN DISTRIBUTION TRANSFORMER | MOBILE TRANSFORMER REPLACEMENT | BANGALA SAHIB ROAD-PANCHKUIAN ROAD RAILWAY COLONY | 71
8 | 25.06.2018 | YVR | 43276.0995 | 43276.1528 | 1:17 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | FIRE IN LTAB | DAMAGED LTAB REPAIRED | ADARSH MOHALLA VIJAY PARK | 1867