## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 27.06.2018 TO 06:00 HRS OF 28.06.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 27.06.2018 | CCK | 43278.4917 | 43278.5542 | 1:30 | HT SYSTEM FAULT | TRIPPING | LT ACB BURNT SAME REPLACED | PART OF TOWN HALL CCK | 1285
2 | 27.06.2018 | DGN | 43278.5883 | 43278.6536 | 1:34 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LTAB FAULTY SAME ATTENDED | BLOCK C-OLD SIMAPURI | 344
3 | 28.06.2018 | DRG | 43279.1059 | 43279.1632 | 1:22 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | TRANSIENT FAULT DUE TO HEAVY RAIN | CHANDNI MAHAL DARYAGANJ | 1591
4 | 28.06.2018 | KRN | 43279.0799 | 43279.1389 | 1:25 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | TRANSIENT FAULT DUE TO HEAVY RAIN | D-BLOCK OLD SEELAMPUR | 2948
5 | 27.06.2018 | KWN | 43278.2569 | 43278.3792 | 2:56 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | JUMPER BROKEN SAME ATTENDED | PHASE-5 & 7 SHIV VIHAR | 518 | FORCE MAJEURE-JUMPER BROKEN DUE TO HEAVY RAIN IN HVDS AREA
6 | 27.06.2018 | KWN | 43278.2604 | 43278.3764 | 2:47 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | HVDS LEAD FAULTY SAME ATTENDED | MUKUND VIHAR | 425 | FORCE MAJEURE-HVDS LEAD FAULTY DUE TO HEAVY RAIN
7 | 27.06.2018 | KWN | 43278.2826 | 43278.3592 | 1:50 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK B-KARAWAL NAGAR | 483
8 | 27.06.2018 | KWN | 43278.2962 | 43278.378 | 1:58 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | SOCKET BURNT SAME REPLACED | CHAMAN PARK KARAWAL NAGAR | 422
9 | 27.06.2018 | KWN | 43278.3269 | 43278.375 | 1:09 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | TRANSIENT FAULT DUE TO HEAVY RAIN | TUNDA NAGAR-BHAGIRATHI VIHAR | 650
10 | 27.06.2018 | KWN | 43278.3803 | 43278.425 | 1:04 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | BADARPUR KHADAR | 35
11 | 27.06.2018 | KWN | 43278.5173 | 43278.5718 | 1:18 | HVDS CABLE & OTHER SYSTEM | FOR REPLACING FAULTY CABLE END BOX | CABLE END BOX REPLACED | BLOCK U-SHIV VIHAR | 128
12 | 27.06.2018 | KWN | 43278.5852 | 43278.6437 | 1:24 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT | MOBILE TRANSFORMER REPLACED | BLOCK C-KHAJURI KHAS | 521
13 | 28.06.2018 | KWN | 43279.0113 | 43279.1103 | 2:23 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | HVDS END BOX FAULTY SAME REPLACED | BIHARIPUR EXTENSION DALLUPRA BLOCK A&B | 355 | FORCE MAJEURE-HVDS END BOX FAULTY NEAR DP BIHARIPUR EXTENSION DUE TO HEAVY RAIN
14 | 28.06.2018 | KWN | 43279.0862 | 43279.1681 | 1:58 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | HVDS FUSE BLOWN SAME REPLACED | BLOCK H-OLD MUSTAFABAD | 1380
15 | 28.06.2018 | KWN | 43279.1859 | 43279.2333 | 1:08 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | HVDS DP FUSE BLOWN SAME REPLACED | KAMAL VIHAR KWR | 871
16 | 28.06.2018 | KWR | 43279.2459 | 43279.3067 | 1:28 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | HVDS LEAD FAULTY SAME ATTENDED | BLOCK D-WEST KARAWAL NAGAR | 124
17 | 28.06.2018 | LNR | 43279.0896 | 43279.1493 | 1:26 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | TRANSIENT FAULT DUE TO HEAVY RAIN | G-BLOCK SHAKARPUR | 897
18 | 27.06.2018 | MVR | 43278.7986 | 43278.8493 | 1:13 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | TRANSIENT FAULT | FISH MARKET GHAZIPUR | 451
19 | 28.06.2018 | MVR | 43279.0243 | 43279.1371 | 2:43 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | FIRE IN LTAB SAME REPAIRED | BLOCK 11-TRILOKPURI PHASE-I | 169 | FORCE MAJEURE- FIRE IN LTAB DUE TO STORM
20 | 27.06.2018 | NNG | 43278.2789 | 43278.3532 | 1:47 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | HVDS LEAD FAULTY SAME ATTENDED | BLOCK E-SEWA DHAM | 860 | FORCE MAJEURE-HVDS LEAD FAULTY DUE TO HEAVY RAIN
21 | 27.06.2018 | NNG | 43278.8532 | 43278.9208 | 1:37 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | TRANSFORMER FUSE BLOWN SAME REPLACED | JYOTI COLONY | 780
22 | 28.06.2018 | PHG | 43279.0553 | 43279.1292 | 1:46 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | SOCKET BURNT SAME REPLACED | IDGAH ROAD PAHARGANJ | 2341
23 | 27.06.2018 | PNR | 43278.3681 | 43278.4773 | 2:37 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | THAKKAR BAPA NAGAR-BLOCK 16 | 1175 | REPAIR OF DAMAGED WIRE ON POLES, TRAFFIC CONGESTION IN AREA
24 | 27.06.2018 | PNR | 43278.6254 | 43278.8365 | 5:04 | DISTRIBUTION TR. | TRANSFORMER LT BUSHING DAMAGED | 990KVA TRANSFORMER REPLACED | TANK ROAD, DEV NAGAR | 1175 | OIL LEAKAGE FROM TRANSFORMER DUE TO DAMAGE OF LT BUSHING. TRANSFORMER REPLACED.
25 | 27.06.2018 | VSE | 43278.3374 | 43278.4194 | 1:58 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | TRANSIENT FAULT DUE TO HEAVY RAIN | BLOCK B-MAYUR VIHAR PHASE III | 1791
26 | 27.06.2018 | VSE | 43278.9765 | 43279.0979 | 2:55 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | HVDS LEAD FAULTY SAME ATTENDED | VILLAGE GHARAULI DIARY | 1791 | FORCE MAJEURE-HVDS LEAD FAULTY DUE TO HEAVY RAIN
27 | 27.06.2018 | YVR | 43278.316 | 43278.4076 | 2:12 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | HVDS LEAD FAULTY SAME ATTENDED | B-BLOCK MAUJPUR | 1554 | FORCE MAJEURE-HVDS LEAD FAULTY DUE TO HEAVY RAIN
28 | 27.06.2018 | YVR | 43278.3177 | 43278.4338 | 2:47 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | TRANSFORMER LT LEAD BURNT SAME ATTENDED | M B ROAD YAMUNA VIHAR | 105 | FORCE MAJEURE-TRANSFORMER LEAD BURNT, TRAFFIC CONGESTION DUE TO HEAVY RAIN
29 | 27.06.2018 | YVR | 43278.3178 | 43278.366 | 1:09 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | TRANSIENT FAULT DUE TO HEAVY RAIN | SUBHASH MOHALLA YVR | 1020
30 | 27.06.2018 | YVR | 43278.6383 | 43278.6817 | 1:02 | LT FEEDER | FOR CONNECTING REPAIRED CABLE | REPAIRED CABLE CONNECTED | JANTA COLONY DWARKAPURI | 98
31 | 28.06.2018 | YVR | 43279.075 | 43279.1368 | 1:29 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | HVDS FUSE BLOWN SAME REPLACED | B-BLOCK GHONDA | 725
32 | 28.06.2018 | YVR | 43279.1011 | 43279.1612 | 1:26 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | TRANSIENT FAULT DUE TO HEAVY RAIN | GAMRI VILLAGE YVR | 1554
33 | 28.06.2018 | YVR | 43279.1035 | 43279.2229 | 2:52 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | TRIPPING | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING | ZERO PUSTA USMANPUR | 1251 | BREAK DOWN DUE TO HEAVY RAIN & WATER LOGGING