## Format
DISCOM : BRPL
OUTAGE REPORT FOR : 16/06/2018 06:00Hr. To 17/06/2018 06:00Hr.
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Area / DT Effected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Detail
1 | 16/06/2018 | SKT | 08:25 | 09:36 | 01:10 | HT SYSTEN FAULT | Grid:66/11kV FATEHPUR BERI GRID To Feeder:11kV FDR O/G NO.-5 RUMALO DEVI , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : ,BHATI KHURD VILLAGE | 544
2 | 16/06/2018 | UMN | 08:35 | 10:21 | 01:45 | HT SYSTEN FAULT | Grid:BINDAPUR (G-3 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-4 , 11KV GRID PANEL,:VCB FLASHED, | RESTORED/ REPAIRED | Part of : UTTAM NAGAR,LAJPAT NAGAR PART III BLOCK C,BLOCK K SANTOSH PARK,SANTOSH PARK_2, | 751
3 | 16/06/2018 | NJF | 09:29 | 10:48 | 01:19 | HT SYSTEN FAULT | Grid:G 4 DWARKA SEC 19 GRID SSTN To Feeder:11kV FDR GOYALA DAIRY , HT O/H,:EARTH WIRE SNAPPED, | RESTORED/ REPAIRED | Part of : ,TAJPUR KHURD_1 | 388
4 | 16/06/2018 | TGN | 10:00 | 12:17 | 02:17 | PLANNED SHUTDOWN | Grid:CHAUKHANDI (33/11kV) GRID SSTN To Feeder:11 kV FDR CHAND NAGAR (KHADDA WALA) , RMU:RMU REPLACEMENT | RESTORED/ REPAIRED | Part of : CHAND NAGAR, | 674
5 | 16/06/2018 | SKT | 10:18 | 11:19 | 01:00 | LT FEEDER | Grid:33kV ADHCHINI GRID To Feeder:11kV FDR SHIVALIK A-BLOCK , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : ,SHIVALIK COLONY_1 | 32
6 | 16/06/2018 | DWK | 10:48 | 12:30 | 01:41 | HVDS CABLE & OTHER SYSTEM | Grid:BINDAPUR (G-3 PPK) (66/11kV) GRID SSTN To Feeder:11KV FDR VISHWASH PARK-2 , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : RAJA PARK MADHU VIHAR,VISHWAS PARK_1,,VISHWAS PARK_5,MAHAVIR ENCLAVE PART II_3,MAHAVIR ENCLAVE II,BLOCK B | 744
7 | 16/06/2018 | VKJ | 10:59 | 12:12 | 01:13 | EMERGENCY SHUTDOWN | Grid:66kV VASANT KUNJ D-BLK GRID To Feeder:11 kV FDR NANGAL DAIRY-2 , LT CIRCUIT:LOAD BALANCING | RESTORED/ REPAIRED | Part of : RANG PURI PAHARI_2, | 102
8 | 16/06/2018 | JKP | 11:20 | 16:00 | 04:40 | PLANNED SHUTDOWN | Grid:MAYAPURI (33/11kV) GRID SSTN To Feeder:11KV SHIV NAGAR , LT CIRCUIT:NETWORK UPGRADTION WORK | RESTORED/ REPAIRED | Part of : SHIV NAGAR, | 58
9 | 16/06/2018 | VKP | 11:21 | 13:01 | 01:39 | EMERGENCY SHUTDOWN | Grid:HASTAL (66/11kV) GRID SSTN To Feeder:11KV FDR A-BLOCK MANDIRWALA , 11KV FEEDER:SAFEGUARDING OF CABLE | RESTORED/ REPAIRED | Part of : ,VIKASPURI BLOCK AG2_1 | 88
10 | 16/06/2018 | SVR | 12:05 | 13:52 | 01:47 | HT SYSTEN FAULT | Grid:JAMIA MILIA (33/11kV) GRID SSTN To Feeder:11kV FDR DENTAL COLLEGE-2 (MEDICAL) , HT O/H,:HTAB FAULTY, | RESTORED/ REPAIRED | Part of : JAMIA MILIIA ISLAMIA UNIVERSITY AREA, | 622
11 | 16/06/2018 | NHP | 12:06 | 13:12 | 01:05 | HT SYSTEN FAULT | Grid:NEHRU PLACE (33/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-5 NEHRU PLACE , RMU,:RMU/HT PANEL FLASH, | RESTORED/ REPAIRED | Part of : NEHRU PLACE_2, | 284
12 | 16/06/2018 | PLM | 12:50 | 13:53 | 01:03 | HT SYSTEN FAULT | Grid:G-7 SECTOR -9 DWARKA To Feeder:11kV FDR HARIJAN BASTI(SHIKSHA BHARTI), EXTN (PLM). , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : PALAM EXTN.PART I, | 711
13 | 16/06/2018 | VKP | 12:58 | 14:27 | 01:29 | EMERGENCY SHUTDOWN | Grid:BODELLA-II GRID To Feeder:11KV DDA TRANSIT CAMP NO.-1 HASTSAL , HVDS:REPAIR/REPLACEMENT WORK OF HVDS CABLE | RESTORED/ REPAIRED | Part of : RAJAN ENCLAVE,PANCHSHIL ENCLAVE, | 564
14 | 16/06/2018 | SKT | 14:16 | 15:44 | 01:27 | LT FEEDER | Grid:66kV IGNOU GRID To Feeder:11kV FDR N-BLOCK SAINIK FARM , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : SAINIK FARM, | 28
15 | 16/06/2018 | DWK | 14:20 | 15:34 | 01:14 | HT SYSTEN FAULT | Grid:G 4 DWARKA SEC 19 GRID SSTN To Feeder:11kV FDR DDA GROUND RMU NO-2 , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : DWARKA SECTOR 6, | 638
16 | 16/06/2018 | DWK | 16:23 | 17:30 | 01:07 | HT SYSTEN FAULT | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR JJ COLONY PH-1 , HT O/H,:BIRDAGE, | RESTORED/ REPAIRED | Part of : JAIN COLONY_2,,SAHYOG VIHAR,PARAM PURI,BLOCK T,JAIN PARK,PAPAN KALAN,SUKH RAM PARK,SUBHASH PARK,JAIN COLONY_1,NANHEY PARK | 603
17 | 16/06/2018 | RKP | 16:29 | 17:38 | 01:09 | HT SYSTEN FAULT | Grid:RIDGE VALLEY (66/33/11kV) GRID SSTN To Feeder:11kV FDR COD , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : MES,B.I.LINE | 369
18 | 16/06/2018 | DWK | 16:54 | 18:29 | 01:34 | LT FEEDER | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR DEEN DAYAL UPADHYAY COLLEGE SECTOR-3 DWARKA , SERVICE LINE,:JUMPER LOOSE/BROKEN FROM DB, | RESTORED/ REPAIRED | Part of : PATEL GARDEN, | 32
19 | 16/06/2018 | NJF | 18:55 | 20:01 | 01:05 | HT SYSTEN FAULT | Grid:DELHI JAL BOARD NAJAFGARH WATER WORKS (66/11) To Feeder:11KV FDR GOYALA SCHOOL , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : SHYAM VIHAR COLONY PHASE-II_1,GOYLA KHURD,SHYAM VIHAR,SHYAM VIHAR COLONY PHASE-I BLOCK--J,SHYAM VIHAR COLONY PHASE-I BLOCK--D,DINDARPUR_1,GURU NANAK NAGAR, | 672
20 | 16/06/2018 | SVR | 22:28 | 23:49 | 01:21 | HT SYSTEN FAULT | Grid:SARAI JULLENA (33/11kV) GRID SSTN To Feeder:11kV FDR SUKHDEV VIHAR , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : ,HAZI COLONY_1,OKHLA VILLAGE | 636
21 | 16/06/2018 | DWK,UMN | 22:38 | 23:59 | 1:21 | EHV TRIPPING | DUE TO BD FROM BINDAPUR TO 20MVA PTR-1 | RESTORED/ REPAIRED | Part of : SITA PURI ,UTTAM NAGR ,JEEVAN PARK ,C 2 JKP .,A-1 MOTHER DAIRY ,VISWAS PARK ,MAHAVIR ENCL ,MADHU VIHAR ,R& S BLK CHANKYA PLACE | 5340
22 | 16/06/2018 | KPR | 23:12 | 00:34 | 01:22 | LT FEEDER | Grid:66 kV OKHLA PHASE-I GRID To Feeder:11kV FDR I-BLOCK, LAL KUAN , DISTRIBUTION TRANSFORMER,:ABNORMAL SOUND FROM THE TRANSFORMER, | RESTORED/ REPAIRED | Part of : LAL KUAN_2, | 158
23 | 16/06/2018 | NHP | 23:47 | 01:11 | 01:23 | LT FEEDER | Grid:EAST OF KAILASH (33/11kV) GRID SSTN To Feeder:11kV FDR O/G INDOOR GARI S/STN , LT ACB,:PROTECTION MALFUNCTION, | RESTORED/ REPAIRED | Part of : ,AMRITPURI (GARHI) | 52
24 | 17/06/2018 | ALN | 00:50 | 02:27 | 01:36 | HT SYSTEN FAULT | Grid:OKHLA (220/66/33/11kV, TRANSCO) PHASE-2 GRID SSTN To Feeder:GOVIND PURI GALI NO.-5 , 11KV GRID PANEL,:PROTECTION MALFUNCTION, | RESTORED/ REPAIRED | Part of : ,GOVIND PURI | 397
25 | 17/06/2018 | NZD | 01:13 | 02:29 | 01:16 | HT SYSTEN FAULT | Grid:EXHIBITION GROUND-I (33/11kV) GRID SSTN To Feeder:TILAK BRIDGE RAILWAY COLONY , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : RAILWAY COLONY TILAK BRIDGE, | 412