## Format
DISCOM : BRPL
OUTAGE REPORT FOR : 24/06/2018 06:00Hr. To 25/06/2018 06:00Hr.
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Area / DT Effected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Detail
1 | 24/06/2018 | SVR | 06:29 | 08:50 | 02:21 | HT SYSTEM FAULT | Grid:66/11KV MEETHAPUR GRID SUB STN To Feeder:11kV FDR GYAN MANDIR , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : SAURAV VIHAR,,MOLARBAND_1, MOLARBAND EXTENSION, | 582
2 | 24/06/2018 | SVR | 07:44 | 09:32 | 01:47 | HVDS CABLE & OTHER SYSTEM | Grid:SARITA VIHAR (66/11kV) GRID SSTN To Feeder:11kV FDR SAHEEN BAGH , HVDS,:HVDS DP FUSE BLOWN, | RESTORED/ REPAIRED | Part of : ,SHAHEEN BAGH,ABDUL FAZAL ENCLAVE PART I_2 | 688
3 | 24/06/2018 | RKP | 07:47 | 08:50 | 01:02 | LT FEEDER | Grid:R.K.PURAM-II (33/11kV) GRID SSTN To Feeder:11kV FDR SECTOR-7 R.K PURAM , LT U/G CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : R K PURAM SECTOR 7, | 46
4 | 24/06/2018 | JKP | 09:09 | 10:34 | 01:24 | HT SYSTEM FAULT | Grid:MAYAPURI (33/11kV) GRID SSTN To Feeder:11KV PUMPING STN. SWARG ASHRAM , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : ,PARAAG VIHAR,HARI ENCLAVE | 529
5 | 24/06/2018 | PLM | 09:36 | 11:16 | 01:39 | LT FEEDER | Grid:G-7 SECTOR -9 DWARKA To Feeder:11KV FDR S/S NO.-5 SECTOR-8 , DISTRIBUTION TRANSFORMER,:LT SOCKET DAMAGED, | RESTORED/ REPAIRED | Part of : RAJ NAGAR EXTENSION_1, | 154
6 | 24/06/2018 | ALN | 10:00 | 16:14 | 06:14 | PLANNED SHUTDOWN | Grid:66 kV OKHLA PHASE-I GRID To Feeder:11 kV FDR S/S NO.-11 O/H , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : ,OKHLA INDUSTRIAL AREA PH I BLOCK B,OKHLA INDUSTRIAL AREA PH I BLOCK A_1 | 114
7 | 24/06/2018 | RKP | 10:00 | 16:53 | 06:53 | PLANNED SHUTDOWN | Grid:RIDGE VALLEY (66/33/11kV) GRID SSTN To Feeder:11kV FDR ST. LTG. NO.-1 , TRANSFORMER:NETWORK UPGRADATION WORK | RESTORED/ REPAIRED | Part of : SUBROTO PARK, | 239
8 | 24/06/2018 | DWK | 10:14 | 11:54 | 01:40 | HT SYSTEM FAULT | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR JAIN COLONY , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : RAJA PARK MADHU VIHAR,JAIN COLONY_2,,SAHYOG VIHAR,JAIN COLONY_1,PAPAN KALAN,SUBHASH PARK,NANHEY PARK,PARAM PURI,BLOCK T | 658
9 | 24/06/2018 | NGL | 11:00 | 14:23 | 03:23 | PLANNED SHUTDOWN | Grid:UDYOG NAGAR (33/11kV) GRID SSTN To Feeder:11kV FDR UDYOG NGR.NO-4 (NEW) , LT CIRCUIT:NETWORK UPGRADTION WORK | RESTORED/ REPAIRED | Part of : UDYOG NAGAR_2, | 527
10 | 24/06/2018 | HKS | 12:00 | 15:56 | 03:56 | PLANNED SHUTDOWN | Grid:33kV SIRI FORT GRID To Feeder:11kV FDR PANCHSHEEL SHOPPING CENTER , TRANSFORMER:TRANSFORMER REPLACEMENT | RESTORED/ REPAIRED | Part of : MAYFAIR GARDEN, | 144
11 | 24/06/2018 | HKS | 14:16 | 16:11 | 01:54 | LT FEEDER | Grid:33kV SIRI FORT GRID To Feeder:11kV FDR E-BLOCK HAUZ KHAS , LT POLE,:CURRENT LEAKAGE, | RESTORED/ REPAIRED | Part of : HAUZ KHAS BLOCK E, | 44
12 | 24/06/2018 | HKS | 14:44 | 16:03 | 01:18 | LT FEEDER | Grid:BHIKAJI CAMA PLACE (33/11kV) GRID SSTN To Feeder:11kV FDR A2/15 SJ.E , LT POLE,:POLE TILTED, | RESTORED/ REPAIRED | Part of : SAFDARJANG ENCLAVE BLOCK A2, | 42
13 | 24/06/2018 | PLM | 15:09 | 16:41 | 01:31 | LT FEEDER | Grid:PAPPANKALAN-I (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR PALAM VILLAGE , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : ,HARIJAN BASTI_3 | 157
14 | 24/06/2018 | PJB | 15:14 | 16:30 | 01:15 | LT FEEDER | Grid:ROHTAK ROAD (NDPL) GRID SSTN To Feeder:ROAD NO- 43 , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : SHIVAJI PARK, | 61
15 | 24/06/2018 | KPR | 16:33 | 17:50 | 01:16 | HT SYSTEM FAULT | Grid:33kV D.C.SAKET GRID To Feeder:11kV FDR MADANGIRI S/S NO.-1 , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : ,MADANGIR CAMP | 732
16 | 24/06/2018 | VKJ | 17:08 | 18:32 | 01:24 | EMERGENCY SHUTDOWN | Grid:66kV C-DOT GRID To Feeder:11 KV FDR NTRO CKT.-1 (OPP. GHITORANI BUS STAND) , HT INTERMEDIATE FEEDER:REPLACEMENT OF JUMPER | RESTORED/ REPAIRED | Part of : GHITORNI_1,ANDHERIA MOR,,FARM HOUSE VASANT KUNJ_1 | 158
17 | 24/06/2018 | VKP | 17:10 | 18:36 | 01:26 | HT SYSTEM FAULT | Grid:HASTAL (66/11kV) GRID SSTN To Feeder:11KV FDR HASTAL VIHAR , DISTRIBUTION TRANSFORMER,:TRANSFORMER LT LEAD BURNT/DAMAGED, | RESTORED/ REPAIRED | Part of : JJ COLONY VIKASPURI_1,OM VIHAR,NAWADA MAJRA, | 704
18 | 24/06/2018 | NZD | 17:48 | 18:57 | 01:09 | HT SYSTEM FAULT | Grid:33kV NDSE-2 GRID To Feeder:11kV FDR G.P.O INA-2+ WAZIR NAGAR GALI NO.-5 , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,KOTLA MUBARAKPUR_1,ARJUN NAGAR,KOTLA MUBARAKPUR VILLAGE | 412
19 | 24/06/2018 | SKT | 17:54 | 18:56 | 01:02 | HT SYSTEM FAULT | Grid:66/11kV FATEHPUR BERI GRID To Feeder:11kV FDR O/G NO.-1 CHADDA MURGI FARM , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : SAHOARPUR VILLAGE,SATBARI VILLAGE_1, SULTANPUR | 864
20 | 24/06/2018 | NHP | 18:22 | 19:31 | 01:08 | HT SYSTEM FAULT | Grid:EAST OF KAILASH (33/11kV) GRID SSTN To Feeder:11kV FDR G-BLOCK EAST OF KAILASH , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : G BLOCK E.O.K., GAR013;S/STN KAILASH HILL | 198
21 | 24/06/2018 | MDK | 19:31 | 20:45 | 01:14 | HT SYSTEM FAULT | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR RAJENDERA PARK , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : TYAGY COLONY,,RAJENDRA PARK EXTN.,NANGLOI EXTN.,RATAN BAGH_1 | 689
22 | 24/06/2018 | PLM | 20:56 | 22:08 | 01:12 | HT SYSTEM FAULT | Grid:PAPPANKALAN-I (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR PALAM VILLAGE , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : DWARKA SECTOR 1,,HARIJAN BASTI_3 | 637
23 | 24/06/2018 | ALN | 21:06 | 22:08 | 01:01 | HT SYSTEM FAULT | Grid:66 kV OKHLA PHASE-I GRID To Feeder:11 kV FDR PUL PRAHALADPUR , LT U/G CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : ,RAILWAY COLONY TUGHLAQABAD | 254
24 | 24/06/2018 | MDK | 21:23 | 22:30 | 01:07 | HT SYSTEM FAULT | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR I.O.C , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,KAVITA COLONY,MUNDKA VILLAGE_2,PUNJABI BASTI WEST DISTRICT,NANGLOI EXTN. | 586
25 | 24/06/2018 | PLM | 21:58 | 23:29 | 01:30 | LT FEEDER | Grid:G-6 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11kV FDR BHATTWALA , LT POLE,:FIRE ON POLE, | RESTORED/ REPAIRED | Part of : RAJ NAGAR EXTENSION_1, | 57
26 | 24/06/2018 | JKP | 22:31 | 23:46 | 01:15 | HT SYSTEM FAULT | Grid:D.C. JANAKPURI (33/11kV) GRID SSTN To Feeder:11KV B-3 JANAKPURI , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,JANAKPURI BLOCK B3B,JANAKPURI BLOCK B3A,FATEH NAGAR,NANGLI JALAB,JANAKPURI BLOCK B3 | 579
27 | 24/06/2018 | JKP | 23:21 | 00:46 | 01:24 | HT SYSTEM FAULT | Grid:HARI NAGAR (66/11kV) GRID SSTN To Feeder:11KV GANDHI PARK , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : HARI NAGAR BLOCK A,,HARI NAGAR BLOCK M,BLOCK B MAYAPURI,MAYAPURI INDUSTRIAL AREA PHASE I,HARI NAGAR BLOCK BE,DELHI MILK SCHEME COLONY,NANAK PURA,HARI NAGAR BLOCK B | 462
28 | 24/06/2018 | DWK | 23:23 | 00:37 | 01:13 | HT SYSTEM FAULT | Grid:PAPPANKALAN-II (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR NAND VIHAR , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : ,BHARAT VIHAR,TRANSIT CAMP,SEC 15,PATEL GARDEN,HARI VIHAR_1,SECTOR 16A_1,TARA NAGAR,HARI VIHAR,SHIVANI ENCLAVE,HARI VIHAR BLOCK- C,UDYOG NAGAR_2,NAND VIHAR,SQUARTER SETTLEMENT | 624
29 | 24/06/2018 | MDK | 23:47 | 00:52 | 01:05 | HT SYSTEM FAULT | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV BAKKARWALA VILLAGE , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,RAJDHANI PARK,NANGLOI EXTN.,VEENA ENCLAVE,AMAR COLONY_2 | 546
30 | 25/06/2018 | NGL | 00:23 | 01:32 | 01:08 | HT SYSTEM FAULT | Grid:UDYOG NAGAR (33/11kV) GRID SSTN To Feeder:11kV FDR O/G S/STN,MIYA WALI NGR , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,MIYANWALI NAGAR BLOCK AB,MIYANWALI NAGAR,MIYANWALI NAGAR BLOCK RR,MIYANWALI NAGAR BLOCK C,MIYANWALI NAGAR BLOCK A3 | 406
31 | 25/06/2018 | DWK | 01:41 | 02:52 | 01:10 | HT SYSTEM FAULT | Grid:BINDAPUR (G-3 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR RAJAPURI SSTN NO-1 , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ,MAHAVIR ENCLAVE PART II_3,MAHAVIR ENCLAVE II,BLOCK B,RAJA PARK MADHU VIHAR,VISHWAS PARK_2,JAIN COLONY_1 | 523
32 | 25/06/2018 | MNG | 03:47 | 05:06 | 01:18 | HT SYSTEM FAULT | Grid:MATIYALA (G-5 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR NWADA , DISTRIBUTION TRANSFORMER,:TRANSFORMER FUSE BLOWN, | RESTORED/ REPAIRED | Part of : ,MOHAN GARDEN BLOCK A,MANSA RAM PARK BLOCK A,MANSA RAM PARK_2 | 861