## Format
DISCOM : BRPL
OUTAGE REPORT FOR : 28/06/2018 06:00Hr. To 29/06/2018 06:00Hr.
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Area / DT Effected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Detail
1 | 28/06/2018 | NZD | 06:00 | 14:00 | 08:00 | PLANNED SHUTDOWN | Grid:33kV NDSE-2 GRID To Feeder:11kV FDR G.P.O INA-2+ WAZIR NAGAR GALI NO.-5 , TRANSFORMER:TRANSFORMER REPLACEMENT | RESTORED/ REPAIRED | Part of : KOTLA MUBARAKPUR_1,ARJUN NAGAR | 368
2 | 28/06/2018 | MDK | 06:16 | 07:51 | 01:34 | HT SYSTEM FAULT | Grid:NANGLOI (66/33/11kV) GRID SSTN To Feeder:11kV FDR I.O.C , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : KAVITA COLONY,PUNJABI BASTI WEST DISTRICT,MUNDKA VILLAGE_2,NANGLOI EXTN. | 649
3 | 28/06/2018 | VKJ | 07:36 | 09:26 | 01:50 | HT SYSTEM FAULT | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR MANAGALPURI , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : ANDHERIA MOR,,FARM HOUSE VASANT KUNJ_1,GHITORNI_1,AYA NAGAR VILLAGE_2,AYA NAGAR VILLAGE_1 | 155
4 | 28/06/2018 | SVR | 09:00 | 10:35 | 01:35 | HT SYSTEM FAULT | Grid:MATHURA ROAD (66/11kV) GRID SSTN To Feeder:11kV FDR BADARPUR O/H , HT O/H,:JUMPER BROKEN, | RESTORED/ REPAIRED | Part of : MCIE | 33
5 | 28/06/2018 | UMN | 10:24 | 11:48 | 01:23 | EMERGENCY SHUTDOWN | Grid:BINDAPUR (G-3 PPK) (66/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-4 , TRANSFORMER:TO ATTEND HOT SPOT | RESTORED/ REPAIRED | Part of : BINDAPUR, | 72
6 | 28/06/2018 | VKP | 10:29 | 11:48 | 01:18 | EMERGENCY SHUTDOWN | Grid:BODELLA-II GRID To Feeder:11KV L.I.G-2 HASTSAL , HVDS:MAINTENANCE | RESTORED/ REPAIRED | Part of : VIJAY VIHAR,OM VIHAR PHASE V,MOHAN GARDEN BLOCK K, | 702
7 | 28/06/2018 | TGN | 10:43 | 15:43 | 05:00 | EMERGENCY SHUTDOWN | Grid:VISHAL (33/11kV) GRID SSTN To Feeder:11kV FDR D-BLOCK RAGHUBIR NAGAR , LT CIRCUIT:REPAIR/REPLACEMENT OF LTAB | RESTORED/ REPAIRED | Part of : RAGHUBIR NAGAR BLOCK R,RAGHUBIR NAGAR_1, | 53
8 | 28/06/2018 | HKS | 10:50 | 11:58 | 01:08 | LT FEEDER | Grid:33kV SIRI FORT GRID To Feeder:11kV FDR N-98. PANCHSHEEL , LT O/H CONDUCTOR,:CONDUCTOR SANPPED, | RESTORED/ REPAIRED | Part of : PUNCHSHILA PARK NORTH | 52
9 | 28/06/2018 | VKJ | 10:53 | 12:44 | 01:50 | EMERGENCY SHUTDOWN | Grid:66kV I.O.C BIJWASAN GRID To Feeder:11 kV FDR BIJWASAN , 11KV FEEDER:PREVENTIVE MAINTENANCE | RESTORED/ REPAIRED | Part of : BIJAWASAN,NAYAK PURA, | 48
10 | 28/06/2018 | RKP | 11:00 | 15:06 | 04:06 | PLANNED SHUTDOWN | Grid:R.K.PURAM-I (33/11kV) GRID SSTN To Feeder:11kV FDR SECTOR-9 R.K PURAM , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : R K PURAM SECTOR 9, | 469
11 | 28/06/2018 | SVR | 11:00 | 17:38 | 06:38 | PLANNED SHUTDOWN | Grid:66/11KV MEETHAPUR GRID SUB STN To Feeder:11kV FDR OM NAGAR GALI NO-10 A B &C BLOCK , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : HARI NAGAR SVR,MOLARBAND_1, | 623
12 | 28/06/2018 | RKP | 11:05 | 12:12 | 01:06 | HT SYSTEM FAULT | Grid:R.K.PURAM-I (33/11kV) GRID SSTN To Feeder:11kV FDR SECTOR-6 R.K PURAM , 11KV GRID PANEL,:BUSBAR FLASH, | RESTORED/ REPAIRED | Part of : MUNIRKA VILLAGE,MUNIRKA,MAYA ENCLAVE BLOCK D A,BLOCK F WEST END,BLOCK B ANAND NIKETAN,WEST END,ANAND NIKETAN,JHARERA,MOTI BAGH,DELHI CANTT,R K PURAM SECTOR 5_1,R K PURAM SECTOR 6,R K PURAM SECTOR 7,R K PURAM SECTOR 8,R K PURAM SECTOR 1,R K PURAM, | 508
13 | 28/06/2018 | PLM | 11:40 | 15:25 | 03:45 | PLANNED SHUTDOWN | Grid:G-2 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11kV FDR POCKET-10 NASEERPUR , LT CIRCUIT:NETWORK UPGRADTION WORK | RESTORED/ REPAIRED | Part of : SAGARPUR WEST,BLOCK RZJ | 62
14 | 28/06/2018 | ALN | 11:47 | 13:28 | 01:40 | LT FEEDER | Grid:33 kV ALAKNANDA GRID To Feeder:11 kV FDR GALI NO.-16 GOVIND PURI , LT ACB,:PHASE NOT COMING OUT, | RESTORED/ REPAIRED | Part of : KALKAJI EXTN BLOCK A10,,KALKAJI EXTENSION_1 | 51
15 | 28/06/2018 | VKP | 11:50 | 13:04 | 01:14 | EMERGENCY SHUTDOWN | Grid:HASTAL (66/11kV) GRID SSTN To Feeder:11KV FDR PRESS ENCLAVE , HVDS:MAINTENANCE | RESTORED/ REPAIRED | Part of : SHIV VIHAR,PANCHSHIL ENCLAVE,VIJAY VIHAR,RAJAN VIHAR, | 668
16 | 28/06/2018 | PJB | 11:52 | 16:22 | 04:29 | EMERGENCY SHUTDOWN | Grid:S.B.MILL (33/11kV) GRID SSTN To Feeder:11kV FDR J.J CLUSTER SHIVA NAND SCHOOL , LT CIRCUIT:REPAIR/REPLACEMENT OF DB AND SERVICE LINE | RESTORED/ REPAIRED | Part of : MANOHAR PARK | 56
17 | 28/06/2018 | NHP | 12:06 | 13:27 | 01:21 | PLANNED SHUTDOWN | Grid:EAST OF KAILASH (33/11kV) GRID SSTN To Feeder:11kV FDR SAI PLAZA , RMU:GAS REFILLING | RESTORED/ REPAIRED | Part of : KALKAJI, | 132
18 | 28/06/2018 | PLM | 12:06 | 15:37 | 03:31 | PLANNED SHUTDOWN | Grid:PAPPANKALAN-I (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR MAHAVIR ENCLAVE , HVDS:MAINTENANCE WORK | RESTORED/ REPAIRED | Part of : MAHAVIR ENCLAVE PART I, | 609
19 | 28/06/2018 | VKJ | 12:15 | 13:40 | 01:25 | PLANNED SHUTDOWN | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR GHITORANI , TRANSFORMER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : GHITORNI_1, | 478
20 | 28/06/2018 | JFR | 12:40 | 16:35 | 03:55 | PLANNED SHUTDOWN | Grid:JAFFARPUR (66/11kV) GRID SSTN To Feeder:11KV NEW MUNDHELA , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : MUNDHELA KHURD,MUNDHELA KALAN, | 629
21 | 28/06/2018 | JFR | 12:40 | 16:35 | 03:55 | PLANNED SHUTDOWN | Grid:JAFFARPUR (66/11kV) GRID SSTN To Feeder:11KV DHANSA , 11KV FEEDER:MAINTENANCE ACTIVITY | RESTORED/ REPAIRED | Part of : BAKARGARH_2,BAKARGARH_1,SAMASPUR KHALSA_2, | 642
22 | 28/06/2018 | NZD | 13:18 | 14:39 | 01:20 | HT SYSTEM FAULT | Grid:EXHIBITION GROUND-I (33/11kV) GRID SSTN To Feeder:BHAIRO ROAD , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : INA COLONY,APPU GHAR,ITO PARKING | 516
23 | 28/06/2018 | VKJ | 13:43 | 15:22 | 01:38 | HT SYSTEM FAULT | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR MANAGALPURI , TRANSIENT FAULT,:TRANSIENT FAULT, | RESTORED/ REPAIRED | Part of : ANDHERIA MOR,,FARM HOUSE VASANT KUNJ_1,GHITORNI_1,AYA NAGAR VILLAGE_2,AYA NAGAR VILLAGE_1 | 155
24 | 28/06/2018 | PJB | 15:24 | 16:41 | 01:16 | HT SYSTEM FAULT | Grid:ROHTAK ROAD (NDPL) GRID SSTN To Feeder:TRANSPORT CENTER , HT CONSUMER,:CONSUMER HT PANEL FLASH, | RESTORED/ REPAIRED | Part of : ELECTRICITY COLONY, | 418
25 | 28/06/2018 | VKJ | 15:34 | 20:06 | 04:32 | EMERGENCY SHUTDOWN | Grid:66kV VASANT KUNJ B-BLK GRID To Feeder:11 kV FDR SECTOR A-2 VASANT KUNJ , LT ACB:ACB REPLACEMENT | RESTORED/ REPAIRED | Part of : MEHRAULI,GANDHI COLONY, | 42
26 | 28/06/2018 | VKJ | 15:41 | 17:12 | 01:31 | HT SYSTEM FAULT | Grid:33kV ANDHERIA BAGH GRID To Feeder:11kV FDR MANAGALPURI , HT O/H,:INSULATOR BROKEN/PUNCTURED, | RESTORED/ REPAIRED | Part of : ANDHERIA MOR,,FARM HOUSE VASANT KUNJ_1,GHITORNI_1,AYA NAGAR VILLAGE_2,AYA NAGAR VILLAGE_1 | 539
27 | 28/06/2018 | PJB | 15:50 | 17:11 | 01:20 | HT SYSTEM FAULT | Grid:PASCHIM PURI (33/11kV) GRID SSTN To Feeder:11KV FDR PEERA GARHI BOOSTER PUMP , HT CONSUMER,:CONSUMER HT PANEL FLASH, | RESTORED/ REPAIRED | Part of : RBI ENCLAVE,PASCHIM VIHAR BLOCK B3,PASCHIM VIHAR BLOCK B1,JAWALAHERI VILLAGE,PASCHIM VIHAR BLOCK BG7,PASCHIM VIHAR BLOCK BG8,PASCHIM VIHAR BLOCK A2,PASCHIM VIHAR MIG FLATS_2,PASCHIM VIHAR BLOCK A4,PIRA GARHI RELIEF CAMP,PASCHIM VIHAR,JAWALAPURI CAMP 5, | 574
28 | 28/06/2018 | ALN | 17:16 | 18:21 | 01:04 | LT FEEDER | Grid:66 kV OKHLA PHASE-I GRID To Feeder:11 kV FDR S/S NO.-A DSIDC OKHLA PH.-1 , LT U/G CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : OKHLA INDUSTRIAL AREA PH I BLOCK C, | 9
29 | 28/06/2018 | ALN | 17:22 | 18:23 | 01:00 | LT FEEDER | Grid:OKHLA PHASE-II (33/11kV) GRID SSTN To Feeder:11kV FDR S/S NO.-8, OKHLA PHASE-1 , LT U/G CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : OKHLA INDUSTRIAL AREA PH I BLOCK B | 14
30 | 28/06/2018 | ALN | 17:38 | 19:07 | 01:28 | LT FEEDER | Grid:66 kV OKHLA PHASE-I GRID To Feeder:11 kV FDR S/S NO.-7 OKHLA PHASE-1 , LT U/G CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : OKHLA INDUSTRIAL AREA PH I BLOCK A_1, | 19
31 | 28/06/2018 | NGL | 19:29 | 20:55 | 01:25 | HT SYSTEM FAULT | Grid:NANGLOI WATER WORKS (66/11kV) GRID SSTN To Feeder:11kV FDR TP KOTLA , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : RANHOLLA,SHAFIPUR RANHOLA VILLAGE_3,RISHAL GARDEN,TILANGAPUR KOTLA VILLAGE_2,TILANGPUR KOTLA VILLAGE,SHAFIPUR RANHOLA VILLAGE_1,BAKKAR WALA VILLAGE_2,PRATAP VIHAR, | 3714
32 | 28/06/2018 | PLM | 19:56 | 21:07 | 01:10 | HVDS CABLE & OTHER SYSTEM | Grid:G-2 PAPPANKALAN (66/11kV) GRID SSTN To Feeder:11kV FDR KAILASH PURI EXTN. , HVDS,:END BOX DAMAGE, | RESTORED/ REPAIRED | Part of : INDRA PARK,,NARSIRPUR,KAILASH PURI,KAILASHPURI WEST,INDRA PARK EXTN,KAILASHPURI MAIN,KAILASHPURI EAST | 475
33 | 28/06/2018 | NHP | 20:24 | 21:42 | 01:17 | HT SYSTEM FAULT | Grid:OKHLA PHASE-II (33/11kV) GRID SSTN To Feeder:11kV FDR DSIDC SCHEME NO.-1 , HT O/H,:TREE TOUCHING, | RESTORED/ REPAIRED | Part of : OKHLA INDUSTRIAL AREA PHASE II, | 160
34 | 28/06/2018 | RKP | 21:03 | 22:06 | 01:02 | LT FEEDER | Grid:R.K.PURAM-II (33/11kV) GRID SSTN To Feeder:11kV FDR SEWA BHAWAN , SERVICE LINE,:JUMPER LOOSE/BROKEN FROM DB, | RESTORED/ REPAIRED | Part of : WEST BLOCK, PUNJABI BAGH | 58
35 | 28/06/2018 | NHP | 21:25 | 22:25 | 01:00 | HT SYSTEM FAULT | Grid:OKHLA PHASE-II (33/11kV) GRID SSTN To Feeder:11kV FDR W-BLOCK OKHLA PHASE-2 , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : MIYANWALI NAGAR BLOCK A1,OKHLA INDUSTRIAL AREA PH II BLOCK Z,OKHLA INDUSTRIAL AREA PH II BLOCK E,OKHLA INDUSTRIAL AREA PH II BLOCK D,OKHLA INDUSTRIAL AREA PH II BLOCK W,OKHLA INDUSTRIAL AREA PH II BLOCK T_1,HARKESH NAGAR_1,OKHLA INDUSTRIAL AREA PHASE III,OKHLA INDUSTRIAL AREA PHASE II, | 438
36 | 28/06/2018 | HKS | 21:27 | 23:14 | 01:47 | HT SYSTEM FAULT | Grid:33kV ADHCHINI GRID To Feeder:11kV FDR SIIA NO.-2 ARCHINI RMU NEAR RED LIGHT , LT ACB,:LT ACB FLASH, | RESTORED/ REPAIRED | Part of : QUTUB INSTITUTIONAL AREA BLOCK C,QUTUB INSTITUTIONAL AREA BLOCK B | 306
37 | 28/06/2018 | VKJ | 22:46 | 23:54 | 01:08 | HT SYSTEM FAULT | Grid:VASANT KUNJ (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11 KV FDR MAHIPAL PUR , 11KV CABLE,:CABLE FAULT, | RESTORED/ REPAIRED | Part of : BLOCK A MAHIPAL PUR EXTN.,MAHIPAL PUR EXTN.,MAHIPAL PUR,NAR SINGH GARDEN BLOCK C, | 582
38 | 28/06/2018 | SVR | 22:49 | 23:59 | 01:09 | HVDS CABLE & OTHER SYSTEM | Grid:SARITA VIHAR (220/66/11kV, TRANSCO) GRID SSTN To Feeder:11kV FDR SOURAV VIHAR-2 , HVDS,:END BOX DAMAGE, | RESTORED/ REPAIRED | Part of : SAURAV VIHAR,HARI NAGAR SVR,MOLARBAND_1, | 619