## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet 1
DISCOM : ___TATA Power-DDL_________
OUTAGE REPORT FOR :___22-06-2018___________
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Details
1 | 2018-06-22 | Bawana | 10:37 | 11:39 | 0.043056 | PLANNED SHUTDOWN | DT Meter Replacement | Restored/Repaired | Parts of : Kanjhawala Village | 2295 | Planned outage
2 | 2018-06-22 | Bawana | 11:03 | 14:52 | 0.15903 | PLANNED SHUTDOWN | For Attending Hot Spot | Restored/Repaired | Parts of : Pooth Khurd Village | 400 | Planned outage
3 | 2018-06-22 | Narela | 06:32 | 07:40 | 0.047222 | HT SYSTEM FAULT | Pin Insulator Broken | Restored/Repaired | Parts of : Tikri Village | 1176 | Interruption due to fault
4 | 2018-06-22 | Keshav Puram | 07:26 | 08:38 | 0.05 | HVDS CABLE & OTHER SYSTEM | HT Jumper Burnt | Restored/Repaired | Parts of : JJ Colony Ashok Vihar | 1429 | Interruption due to fault
5 | 2018-06-22 | Narela | 09:46 | 15:20 | 0.23194 | PLANNED SHUTDOWN | HT Pole Replacement | Restored/Repaired | Parts of : Khera Khurd | 925 | Scheduled system maintenance
6 | 2018-06-22 | Shalimar Bagh | 12:26 | 14:20 | 0.079167 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Burari Village | 593 | Scheduled system maintenance
7 | 2018-06-22 | Bawana | 13:08 | 14:25 | 0.053472 | HVDS CABLE & OTHER SYSTEM | HT Jumper Sparking | Restored/Repaired | Parts of : Shiv Vihar | 2269 | Interruption due to fault
8 | 2018-06-22 | Shalimar Bagh | 14:32 | 15:40 | 0.047222 | HVDS CABLE & OTHER SYSTEM | HT Socket Burnt | Restored/Repaired | Parts of : Upkar Colony | 1422 | Interruption due to fault
9 | 2018-06-22 | Narela | 16:47 | 18:39 | 0.077778 | DISTRIBUTION TR. | HT Lead Burnt | Restored/Repaired | Parts of : Holambi Khurd | 2075 | Interruption due to fault
10 | 2018-06-22 | Badli | 16:45 | 18:23 | 0.068056 | HT SYSTEM FAULT | Squirrel Electrocuted | Restored/Repaired | Parts of : Sec 26 Rohini | 1145 | Interruption due to fault
11 | 2018-06-22 | Moti Nagar | 16:45 | 18:00 | 0.052083 | HVDS CABLE & OTHER SYSTEM | HT Jumper Burnt | Restored/Repaired | Parts of : Inderpuri | 680 | Interruption due to fault
12 | 2018-06-22 | Shalimar Bagh | 10:37 | 15:30 | 0.20347 | PLANNED SHUTDOWN | LT ABC Replacement | Restored/Repaired | Parts of : 9 B Block Shalimar Bagh | 405 | Scheduled system maintenance
13 | 2018-06-22 | Narela | 00:18 | 0.09375 | 0.08125 | LT FEEDER | LT ABC Burnt | Restored/Repaired | Parts of : Narela | 394 | Interruption due to fault
14 | 2018-06-22 | Shalimar Bagh | 00:26 | 0.083333 | 0.065278 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Jumper Burnt | Restored/Repaired | Parts of : Bangali Colony | 839 | Interruption due to fault
15 | 2018-06-22 | Keshav Puram | 00:58 | 04:00 | 0.12639 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire at Pole | Restored/Repaired | Parts of : C 5 Lawrence Road | 339 | Force majeure due to fire
16 | 2018-06-22 | Narela | 02:32 | 0.15972 | 0.054167 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Jumper Sparking | Restored/Repaired | Parts of : Alipur | 305 | Interruption due to fault
17 | 2018-06-22 | Narela | 03:11 | 0.20833 | 0.075694 | LT FEEDER | LT Cable Burnt | Restored/Repaired | Parts of : Vasu Vihar | 476 | Interruption due to fault
18 | 2018-06-22 | Bawana | 05:37 | 07:00 | 0.057639 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | Tyco Box Burnt | Restored/Repaired | Parts of : Surat Vihar | 874 | Interruption due to fault
19 | 2018-06-22 | Narela | 09:58 | 0.48611 | 0.070833 | LT FEEDER | MCCB Faulty | Restored/Repaired | Parts of : Mukhmel Pur | 407 | Interruption due to fault
20 | 2018-06-22 | Shalimar Bagh | 11:39 | 13:30 | 0.077083 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | Tyco Box Burnt | Restored/Repaired | Parts of : Sant Nagar | 328 | Interruption due to fault
21 | 2018-06-22 | Mangolpuri | 12:19 | 14:21 | 0.084722 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Raj Park | 648 | Scheduled system maintenance
22 | 2018-06-22 | Bawana | 12:29 | 0.65625 | 0.13611 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Rama Vihar | 593 | Scheduled system maintenance
23 | 2018-06-22 | Keshav Puram | 15:28 | 0.69097 | 0.046528 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Socket Burnt | Restored/Repaired | Parts of : Lal Market | 437 | Interruption due to fault
24 | 2018-06-22 | Mangolpuri | 15:28 | 0.70833 | 0.063889 | LT FEEDER | LT Cable Burnt | Restored/Repaired | Parts of : Pooth Kalan | 588 | Interruption due to fault
25 | 2018-06-22 | Model Town | 15:57 | 17:04 | 0.046528 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | IPC Burnt | Restored/Repaired | Parts of : Mukherjee Nagar | 325 | Interruption due to fault
26 | 2018-06-22 | Model Town | 00:43 | 02:34 | 0.077083 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | Tyco Box Burnt | Restored/Repaired | Parts of : Azadpur | 620 | Interruption due to fault
27 | 2018-06-22 | Civil Lines | 11:47 | 0.70833 | 0.21736 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | LT Pole Broken by Unknown Vehicle | Restored/Repaired | Parts of : Punjabi Basti | 559 | Force majeure due to sabotage
28 | 2018-06-22 | Rohini | 14:12 | 17:18 | 0.12917 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : B Block Avantika | 733 | Scheduled system maintenance
29 | 2018-06-22 | Pitam Pura | 14:47 | 16:09 | 0.056944 | LT FEEDER | LT ABC Burnt | Restored/Repaired | Parts of : Rani Bagh | 363 | Interruption due to fault
30 | 2018-06-22 | Shalimar Bagh | 15:15 | 0.6875 | 0.052083 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Kamal Vihar | 387 | Scheduled system maintenance
31 | 2018-06-22 | Rohini | 16:50 | 18:46 | 0.080556 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | Bus Bar Burnt | Restored/Repaired | Parts of : Sec 6 Rohini | 616 | Interruption due to fault
32 | 2018-06-22 | Rohini | 17:24 | 18:26 | 0.043056 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Jumper Burnt | Restored/Repaired | Parts of : Sec 7 Rohini | 642 | Interruption due to fault
33 | 2018-06-22 | Civil Lines | 18:13 | 19:21 | 0.047222 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | CT Meter Burnt | Restored/Repaired | Parts of : Roshanara Road | 302 | Interruption due to fault

## Sheet3 (hidden)
43105.5833 | 43105.6319 | 01:10 | 1:10
43105.7257 | 43105.8056 | 01:55 | 1:55
43105.4215 | 43105.7167 | 07:05 | 7:05
43105.4778 | 43105.7083 | 05:32 | 5:32
43105.4618 | 43105.7479 | 06:52 | 6:52
43105.5479 | 43105.625 | 01:51 | 1:51
43105.5035 | 43105.7118 | 05:00 | 5:00
43105.5146 | 43105.6833 | 04:03 | 4:03
43105.4764 | 43105.5667 | 02:10 | 2:10
43105.5257 | 43105.5972 | 01:43 | 1:43
43105.5049 | 43105.625 | 02:53 | 2:53
43105.2021 | 43105.3021 | 02:24 | 2:24
43105.3757 | 43105.4653 | 02:09 | 2:09
43105.4167 | 43105.7042 | 06:54 | 6:54
43105.4347 | 43105.6667 | 05:34 | 5:34
43105.5299 | 43105.6167 | 02:05 | 2:05
43105.5507 | 43105.6215 | 01:42 | 1:42
43105.6049 | 43105.6632 | 01:24 | 1:24
43105.6417 | 43105.7882 | 03:31 | 3:31
43105.8743 | 43105.9479 | 01:46 | 1:46
0.49514 | 0.55417 | 1:25 | 1:25
0.45694 | 0.71389 | 6:10 | 6:10
0.50486 | 0.59653 | 2:12 | 2:12
0.53542 | 0.72222 | 4:29 | 4:29
0.57708 | 0.625 | 1:09 | 1:09

## Sheet2 (hidden)
42976.2569 | 42976.3056 | 01:10 | 1:10
42976.2389 | 42976.2812 | 01:01 | 1:01
42976.241 | 42976.2882 | 01:08 | 1:08
42976.2833 | 42976.3403 | 01:22 | 1:22
42976.3438 | 42976.4035 | 01:26 | 1:26
42976.4896 | 42976.5896 | 02:24 | 2:24
42976.7535 | 42976.7986 | 01:05 | 1:05
42976.4215 | 42976.655 | 05:36 | 5:36
42976.3403 | 42976.5208 | 04:20 | 4:20
42976.4472 | 42976.7087 | 06:16 | 6:17
42976.3208 | 42976.3929 | 01:43 | 1:44
42976.3288 | 42976.3796 | 01:13 | 1:13
42976.3591 | 42976.4029 | 01:03 | 1:03
42976.5701 | 42976.6737 | 02:29 | 2:29
42976.4215 | 42976.5654 | 03:27 | 3:27
42976.5461 | 42976.5916 | 01:05 | 1:06
42976.5975 | 42976.7538 | 03:45 | 3:45
42976.906 | 42976.9657 | 01:26 | 1:26
19:00 | 20:30 | 1:30 | 1:30
13:03 | 17:40 | 4:37 | 4:37
13:55 | 15:22 | 1:27 | 1:27
14:39 | 17:00 | 2:21 | 2:21
15:13 | 16:27 | 1:14 | 1:14
11:18 | 17:05 | 5:47 | 5:47
11:19 | 16:00 | 4:41 | 4:41
12:24 | 14:08 | 1:44 | 1:44
23:05 | 0:17 | 1:12 | -0.95
22:25 | 23:48 | 1:23 | 1:23
13:49 | 15:40 | 1:51 | 1:51