## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet 1
DISCOM : ___TATA Power-DDL_________
OUTAGE REPORT FOR :___29-06-2018___________
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Details
1 | 2018-06-29 | Shalimar Bagh | 16:23 | 17:57 | 0.065278 | PLANNED SHUTDOWN | For Connecting New HT Cable | Restored/Repaired | Parts of : Tomar Colony | 2395 | Planned outage
2 | 2018-06-29 | Narela | 13:19 | 17:57 | 0.19306 | PLANNED SHUTDOWN | DT Maintenance | Restored/Repaired | Parts of : Nangli Poona | 4041 | Planned outage
3 | 2018-06-29 | Shakti Nagar | 08:18 | 11:20 | 0.12639 | PLANNED SHUTDOWN | DT Replacement | Restored/Repaired | Parts of : Gulabi Bagh | 615 | Planned outage
4 | 2018-06-29 | Shalimar Bagh | 11:51 | 14:20 | 0.10347 | PLANNED SHUTDOWN | Relay Replacement | Restored/Repaired | Parts of : Swaroop Nagar | 641 | Planned outage
5 | 2018-06-29 | Badli | 10:17 | 12:25 | 0.088889 | PLANNED SHUTDOWN | Pin Insulator Replacement | Restored/Repaired | Parts of : Sec 16 Rohini | 420 | Planned outage
6 | 2018-06-29 | Bawana | 11:25 | 13:03 | 0.068056 | PLANNED SHUTDOWN | For DT Oil Top up | Restored/Repaired | Parts of : Pooth Khurd Village | 1099 | Planned outage
7 | 2018-06-29 | Shalimar Bagh | 10:00 | 12:02 | 0.084722 | PLANNED SHUTDOWN | DD Unit Replacement | Restored/Repaired | Parts of : Kamal Vihar | 419 | Planned outage
8 | 2018-06-29 | Mangolpuri | 06:54 | 09:50 | 0.12222 | PLANNED SHUTDOWN | DT Meter Replacement | Restored/Repaired | Parts of : Mangolpuri | 1354 | Planned outage
9 | 2018-06-29 | Moti Nagar | 06:26 | 07:30 | 0.044444 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | External Object Fell on Line | Restored/Repaired | Parts of : Kirbi Place | 421 | Force majeure due to sabotage
10 | 2018-06-29 | Shakti Nagar | 03:00 | 04:15 | 0.052083 | HT SYSTEM FAULT | HT ABC Burnt | Restored/Repaired | Parts of : Shastri Nagar | 734 | Interruption due to fault
11 | 2018-06-29 | Narela | 03:38 | 05:52 | 0.093056 | HT SYSTEM FAULT | HT Termination Faulty | Restored/Repaired | Parts of : Bakhtawarpur Village | 1234 | Interruption due to fault
12 | 2018-06-29 | Bawana | 06:56 | 08:50 | 0.079167 | HVDS CABLE & OTHER SYSTEM | DD Unit Broken | Restored/Repaired | Parts of : Auchandi Village | 586 | Interruption due to fault
13 | 2018-06-29 | Mangolpuri | 12:27 | 19:10 | 0.27986 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | HT Pole Broken by Unknown Vehicle | Restored/Repaired | Parts of : Budh Vihar | 401 | Force majeure due to sabotage
14 | 2018-06-29 | Civil Lines | 12:53 | 14:30 | 0.067361 | DISTRIBUTION TR. | LT ACB Faulty | Restored/Repaired | Parts of : DU Staff Quarters | 530 | Interruption due to fault
15 | 2018-06-29 | Bawana | 13:12 | 15:30 | 0.095833 | PLANNED SHUTDOWN | For Attending Hot Spot | Restored/Repaired | Parts of : Inderraj Enclave | 787 | Scheduled system maintenance
16 | 2018-06-29 | Badli | 13:12 | 15:10 | 0.081944 | HT SYSTEM FAULT | HT Conductor Broken | Restored/Repaired | Parts of : Krishana Colony | 890 | Interruption due to fault
17 | 2018-06-29 | Moti Nagar | 13:34 | 15:18 | 0.072222 | HT SYSTEM FAULT | HT ABC Burnt | Restored/Repaired | Parts of : Ranjit Nagar | 836 | Interruption due to fault
18 | 2018-06-29 | Bawana | 13:57 | 22:32 | 0.35764 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire in LT ACB | Restored/Repaired | Parts of : Karala Village | 917 | Force majeure due to fire
19 | 2018-06-29 | Shalimar Bagh | 14:49 | 15:54 | 0.045139 | HVDS CABLE & OTHER SYSTEM | HT Jumper Burnt | Restored/Repaired | Parts of : Jharodha Village | 2431 | Interruption due to fault
20 | 2018-06-29 | Moti Nagar | 16:12 | 18:20 | 0.088889 | HVDS CABLE & OTHER SYSTEM | HT Socket Burnt | Restored/Repaired | Parts of : Rama Road | 1082 | Interruption due to fault
21 | 2018-06-29 | Bawana | 16:58 | 20:30 | 0.14722 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire at Pole | Restored/Repaired | Parts of : Shiv Vihar | 2510 | Force majeure due to fire
22 | 2018-06-29 | Shalimar Bagh | 07:13 | 08:30 | 0.053472 | HVDS CABLE & OTHER SYSTEM | HT Jumper Sparking | Restored/Repaired | Parts of : I & J Block Jahangirpuri | 3034 | Interruption due to fault
23 | 2018-06-29 | Shalimar Bagh | 11:42 | 12:50 | 0.047222 | PLANNED SHUTDOWN | Oil Leakage in DT | Restored/Repaired | Parts of : Sanjay Enclave | 868 | Scheduled system maintenance
24 | 2018-06-29 | Moti Nagar | 10:48 | 12:30 | 0.070833 | HT SYSTEM FAULT | HT Cable Burnt | Restored/Repaired | Parts of : Todapur | 321 | Interruption due to fault
25 | 2018-06-29 | Narela | 14:29 | 0.67014 | 0.066667 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Jumper Burnt | Restored/Repaired | Parts of : swatantra Nagar | 506 | Interruption due to fault
26 | 2018-06-29 | Mangolpuri | 16:03 | 17:20 | 0.053472 | LT FEEDER | LT Cable Burnt | Restored/Repaired | Parts of : Rajiv Nagar | 550 | Interruption due to fault
27 | 2018-06-29 | Narela | 16:16 | 0.72917 | 0.051389 | LT FEEDER | LT ABC Burnt | Restored/Repaired | Parts of : Hamid Pur | 626 | Interruption due to fault
28 | 2018-06-29 | Bawana | 17:23 | 20:40 | 0.13681 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire at Pole | Restored/Repaired | Parts of : Punjab Khor | 381 | Force majeure due to fire
29 | 2018-06-29 | Mangolpuri | 18:05 | 0.82639 | 0.072917 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | Tyco Box Burnt | Restored/Repaired | Parts of : Begumpur | 335 | Interruption due to fault
30 | 2018-06-29 | Mangolpuri | 12:07 | 0.58333 | 0.078472 | PLANNED SHUTDOWN | LT Load Balancing | Restored/Repaired | Parts of : Sultanpuri | 371 | Scheduled system maintenance

## Sheet3 (hidden)
43105.5833 | 43105.6319 | 01:10 | 1:10
43105.7257 | 43105.8056 | 01:55 | 1:55
43105.4215 | 43105.7167 | 07:05 | 7:05
43105.4778 | 43105.7083 | 05:32 | 5:32
43105.4618 | 43105.7479 | 06:52 | 6:52
43105.5479 | 43105.625 | 01:51 | 1:51
43105.5035 | 43105.7118 | 05:00 | 5:00
43105.5146 | 43105.6833 | 04:03 | 4:03
43105.4764 | 43105.5667 | 02:10 | 2:10
43105.5257 | 43105.5972 | 01:43 | 1:43
43105.5049 | 43105.625 | 02:53 | 2:53
43105.2021 | 43105.3021 | 02:24 | 2:24
43105.3757 | 43105.4653 | 02:09 | 2:09
43105.4167 | 43105.7042 | 06:54 | 6:54
43105.4347 | 43105.6667 | 05:34 | 5:34
43105.5299 | 43105.6167 | 02:05 | 2:05
43105.5507 | 43105.6215 | 01:42 | 1:42
43105.6049 | 43105.6632 | 01:24 | 1:24
43105.6417 | 43105.7882 | 03:31 | 3:31
43105.8743 | 43105.9479 | 01:46 | 1:46
0.49514 | 0.55417 | 1:25 | 1:25
0.45694 | 0.71389 | 6:10 | 6:10
0.50486 | 0.59653 | 2:12 | 2:12
0.53542 | 0.72222 | 4:29 | 4:29
0.57708 | 0.625 | 1:09 | 1:09

## Sheet2 (hidden)
42976.2569 | 42976.3056 | 01:10 | 1:10
42976.2389 | 42976.2812 | 01:01 | 1:01
42976.241 | 42976.2882 | 01:08 | 1:08
42976.2833 | 42976.3403 | 01:22 | 1:22
42976.3438 | 42976.4035 | 01:26 | 1:26
42976.4896 | 42976.5896 | 02:24 | 2:24
42976.7535 | 42976.7986 | 01:05 | 1:05
42976.4215 | 42976.655 | 05:36 | 5:36
42976.3403 | 42976.5208 | 04:20 | 4:20
42976.4472 | 42976.7087 | 06:16 | 6:17
42976.3208 | 42976.3929 | 01:43 | 1:44
42976.3288 | 42976.3796 | 01:13 | 1:13
42976.3591 | 42976.4029 | 01:03 | 1:03
42976.5701 | 42976.6737 | 02:29 | 2:29
42976.4215 | 42976.5654 | 03:27 | 3:27
42976.5461 | 42976.5916 | 01:05 | 1:06
42976.5975 | 42976.7538 | 03:45 | 3:45
42976.906 | 42976.9657 | 01:26 | 1:26
19:00 | 20:30 | 1:30 | 1:30
13:03 | 17:40 | 4:37 | 4:37
13:55 | 15:22 | 1:27 | 1:27
14:39 | 17:00 | 2:21 | 2:21
15:13 | 16:27 | 1:14 | 1:14
11:18 | 17:05 | 5:47 | 5:47
11:19 | 16:00 | 4:41 | 4:41
12:24 | 14:08 | 1:44 | 1:44
23:05 | 0:17 | 1:12 | -0.95
22:25 | 23:48 | 1:23 | 1:23
13:49 | 15:40 | 1:51 | 1:51