## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet 1
DISCOM : ___TATA Power-DDL_________
OUTAGE REPORT FOR :___30-06-2018___________
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
[6 empty] | Main Reason | Details
1 | 2018-06-30 | Bawana | 08:39 | 16:41 | 0.33472 | PLANNED SHUTDOWN | HT ABC Replacement | Restored/Repaired | Parts of : A Block JJ Colony Bawana | 8851 | Planned outage
2 | 2018-06-30 | Shalimar Bagh | 10:50 | 15:35 | 0.19792 | PLANNED SHUTDOWN | DT Replacement | Restored/Repaired | Parts of : Laxmi Vihar | 705 | Planned outage
3 | 2018-06-30 | Bawana | 0.40903 | 17:58 | 0.33958 | PLANNED SHUTDOWN | HT Line Extension | Restored/Repaired | Parts of : Sec 1 Bawana | 325 | Planned outage
4 | 2018-06-30 | Badli | 10:55 | 12:30 | 0.065972 | PLANNED SHUTDOWN | Relay Replacement | Restored/Repaired | Parts of : Badli Village | 478 | Planned outage
5 | 2018-06-30 | Mangolpuri | 10:00 | 17:15 | 0.30208 | PLANNED SHUTDOWN | GO Switch Replacement | Restored/Repaired | Parts of : Pooth Kalan | 4638 | Planned outage
6 | 2018-06-30 | Bawana | 08:26 | 10:15 | 0.075694 | HT SYSTEM FAULT | HT ABC Burnt | Restored/Repaired | Parts of : Jain Nagar | 888 | Interruption due to fault
7 | 2018-06-30 | Keshav Puram | 08:41 | 09:55 | 0.051389 | HVDS CABLE & OTHER SYSTEM | HT Socket Burnt | Restored/Repaired | Parts of : Shanti Nagar | 356 | Interruption due to fault
8 | 2018-06-30 | Shalimar Bagh | 09:02 | 11:50 | 0.11667 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire at Pole | Restored/Repaired | Parts of : C Block Shalimar Bagh | 1740 | Force majeure due to fire
9 | 2018-06-30 | Bawana | 08:02 | 0.39653 | 0.061806 | HT SYSTEM FAULT | HT ABC Burnt | Restored/Repaired | Parts of : Agar Nagar | 2910 | Interruption due to fault
10 | 2018-06-30 | Narela | 11:03 | 14:00 | 0.12292 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | HT Pole Broken by Unknown Vehicle | Restored/Repaired | Parts of : Alipur | 1234 | Force majeure due to sabotage
11 | 2018-06-30 | Rohini | 12:11 | 13:15 | 0.044444 | HT SYSTEM FAULT | GO Switch Sparking | Restored/Repaired | Parts of : Rithala | 428 | Interruption due to fault
12 | 2018-06-30 | Bawana | 12:11 | 0.55417 | 0.046528 | HVDS CABLE & OTHER SYSTEM | HT Jumper Burnt | Restored/Repaired | Parts of : Inder Enclave | 6963 | Interruption due to fault
13 | 2018-06-30 | Shalimar Bagh | 11:51 | 14:20 | 0.10347 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | External Object fell on Line | Restored/Repaired | Parts of : Jahangirpuri | 388 | Force majeure due to sabotage
14 | 2018-06-30 | Bawana | 13:05 | 14:10 | 0.045139 | HT SYSTEM FAULT | HT Conductor Broken | Restored/Repaired | Parts of : Nangal Village | 4645 | Interruption due to fault
15 | 2018-06-30 | Narela | 13:26 | 14:55 | 0.061806 | HT SYSTEM FAULT | Birdage | Restored/Repaired | Parts of : Holambi Kalan | 2482 | Interruption due to fault
16 | 2018-06-30 | Mangolpuri | 17:51 | 19:30 | 0.06875 | HT SYSTEM FAULT | HT ABC Burnt | Restored/Repaired | Parts of : Budh Vihar | 1328 | Interruption due to fault
17 | 2018-06-30 | Pitam Pura | 03:28 | 0.22569 | 0.08125 | HT SYSTEM FAULT | HT Cable Faulty | Restored/Repaired | Parts of : Rani Bagh | 509 | Interruption due to fault
18 | 2018-06-30 | Model Town | 09:34 | 11:30 | 0.080556 | HVDS CABLE & OTHER SYSTEM | HT Jumper Burnt | Restored/Repaired | Parts of : G 1 GTK Road | 301 | Interruption due to fault
19 | 2018-06-30 | Shalimar Bagh | 11:20 | 14:54 | 0.14861 | FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.) | Fire at Pole | Restored/Repaired | Parts of : Milan Vihar | 484 | Force majeure due to fire
20 | 2018-06-30 | Mangolpuri | 13:08 | 14:26 | 0.054167 | LT FEEDER | LT Cable Faulty | Restored/Repaired | Parts of : Sec 20 Rohini | 576 | Interruption due to fault
21 | 2018-06-30 | Shalimar Bagh | 14:46 | 0.66667 | 0.051389 | LT FEEDER | LT ABC Burnt | Restored/Repaired | Parts of : Mukundpur | 922 | Interruption due to fault
22 | 2018-06-30 | Model Town | 14:30 | 16:29 | 0.082639 | PLANNED SHUTDOWN | LT Bus Bar Replacement | Restored/Repaired | Parts of : A Block Mahendru Enclave | 592 | Scheduled system maintenance
23 | 2018-06-30 | Narela | 14:59 | 0.67708 | 0.052778 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT socket Burnt | Restored/Repaired | Parts of : Kushak Hiranki | 527 | Interruption due to fault
24 | 2018-06-30 | Pitam Pura | 12:36 | 15:23 | 0.11597 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Rishi Nagar | 364 | Scheduled system maintenance
25 | 2018-06-30 | Badli | 21:42 | 23:15 | 0.064583 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Jumper Burnt | Restored/Repaired | Parts of : Sec 26 Rohini | 947 | Interruption due to fault
26 | 2018-06-30 | Bawana | 12:06 | 14:00 | 0.079167 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | LT Jumper Burnt | Restored/Repaired | Parts of : Meer Vihar | 844 | Interruption due to fault
27 | 2018-06-30 | Moti Nagar | 12:09 | 14:40 | 0.10486 | PLANNED SHUTDOWN | Load Balancing | Restored/Repaired | Parts of : Patel Nagar | 367 | Scheduled system maintenance
28 | 2018-06-30 | Keshav Puram | 16:07 | 0.75 | 0.078472 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | Tyco Box Burnt | Restored/Repaired | Parts of : Kanhaiya Nagar | 735 | Interruption due to fault

## Sheet3 (hidden)
43105.5833 | 43105.6319 | 01:10 | 1:10
43105.7257 | 43105.8056 | 01:55 | 1:55
43105.4215 | 43105.7167 | 07:05 | 7:05
43105.4778 | 43105.7083 | 05:32 | 5:32
43105.4618 | 43105.7479 | 06:52 | 6:52
43105.5479 | 43105.625 | 01:51 | 1:51
43105.5035 | 43105.7118 | 05:00 | 5:00
43105.5146 | 43105.6833 | 04:03 | 4:03
43105.4764 | 43105.5667 | 02:10 | 2:10
43105.5257 | 43105.5972 | 01:43 | 1:43
43105.5049 | 43105.625 | 02:53 | 2:53
43105.2021 | 43105.3021 | 02:24 | 2:24
43105.3757 | 43105.4653 | 02:09 | 2:09
43105.4167 | 43105.7042 | 06:54 | 6:54
43105.4347 | 43105.6667 | 05:34 | 5:34
43105.5299 | 43105.6167 | 02:05 | 2:05
43105.5507 | 43105.6215 | 01:42 | 1:42
43105.6049 | 43105.6632 | 01:24 | 1:24
43105.6417 | 43105.7882 | 03:31 | 3:31
43105.8743 | 43105.9479 | 01:46 | 1:46
0.49514 | 0.55417 | 1:25 | 1:25
0.45694 | 0.71389 | 6:10 | 6:10
0.50486 | 0.59653 | 2:12 | 2:12
0.53542 | 0.72222 | 4:29 | 4:29
0.57708 | 0.625 | 1:09 | 1:09

## Sheet2 (hidden)
42976.2569 | 42976.3056 | 01:10 | 1:10
42976.2389 | 42976.2812 | 01:01 | 1:01
42976.241 | 42976.2882 | 01:08 | 1:08
42976.2833 | 42976.3403 | 01:22 | 1:22
42976.3438 | 42976.4035 | 01:26 | 1:26
42976.4896 | 42976.5896 | 02:24 | 2:24
42976.7535 | 42976.7986 | 01:05 | 1:05
42976.4215 | 42976.655 | 05:36 | 5:36
42976.3403 | 42976.5208 | 04:20 | 4:20
42976.4472 | 42976.7087 | 06:16 | 6:17
42976.3208 | 42976.3929 | 01:43 | 1:44
42976.3288 | 42976.3796 | 01:13 | 1:13
42976.3591 | 42976.4029 | 01:03 | 1:03
42976.5701 | 42976.6737 | 02:29 | 2:29
42976.4215 | 42976.5654 | 03:27 | 3:27
42976.5461 | 42976.5916 | 01:05 | 1:06
42976.5975 | 42976.7538 | 03:45 | 3:45
42976.906 | 42976.9657 | 01:26 | 1:26
19:00 | 20:30 | 1:30 | 1:30
13:03 | 17:40 | 4:37 | 4:37
13:55 | 15:22 | 1:27 | 1:27
14:39 | 17:00 | 2:21 | 2:21
15:13 | 16:27 | 1:14 | 1:14
11:18 | 17:05 | 5:47 | 5:47
11:19 | 16:00 | 4:41 | 4:41
12:24 | 14:08 | 1:44 | 1:44
23:05 | 0:17 | 1:12 | -0.95
22:25 | 23:48 | 1:23 | 1:23
13:49 | 15:40 | 1:51 | 1:51