## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet3
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 04.03.2018 TO 06:00 HRS OF 05.03.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 04.03.2018 | CCK | 43163.4647 | 43163.5287 | 1:32 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | LAJPAT RAI MARKET
2 | 04.03.2018 | CCK | 43163.4665 | 43163.5375 | 1:42 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | HAUZ QAZI-CHANDNI CHOWK
3 | 04.03.2018 | CCK | 43163.5382 | 43163.6092 | 1:42 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | ZEENAT BARI-MORI GATE
4 | 04.03.2018 | DGN | 43163.3611 | 43163.4052 | 1:03 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | BLOCK J & K-DILSHAD GARDEN
5 | 05.03.2018 | KKD | 43164.0048 | 43164.1951 | 4:34 | DISTRIBUTION TR. | 990KVA T/F FAULTY | TRANSFORMER REPLACED BY MOBILE TRANSFORMER | BAZAAR GALI KKD |  | 990KVA T/F FAULTY SAME REPLACED BY MOBILE TRANSFORMER
6 | 04.03.2018 | KWN | 43163.4372 | 43163.5103 | 1:45 | HVDS CABLE & OTHER SYSTEM | 25KVA HVDS TRANSFORMER FAULTY | HVDS TRANSFORMER REPLACED | BLOCK B-OLD MUSTAFABAD
7 | 04.03.2018 | NNG | 43163.4666 | 43163.5345 | 1:38 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | NEW MANDOLI INDUSTRIAL AREA
8 | 04.03.2018 | NNG | 43163.6034 | 43163.6819 | 1:53 | HVDS CABLE & OTHER SYSTEM | HVDS CABLE FAULTY | HVDS CABLE REPAIRED | BLOCK A-SEWA DHAM
9 | 04.03.2018 | PHG | 43163.4604 | 43163.6669 | 4:57 | HT SYSTEM FAULT | HT POLE DAMAGED BY UNKNOWN VEHICLE | DAMAGED POLE REPLACED | PHARI DHIRAJ-SADAR BAZAR |  | HT POLE DAMAGED BY UNKNOWN VEHICLE SAME REPLACED
10 | 04.03.2018 | YVR | 43163.5194 | 43163.5764 | 1:22 | HT SYSTEM FAULT | TRIPPING | CONSUMER HT PANEL FLASHED | GHONDA PATTI CHAUHAN