## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet3
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 11.03.2018 TO 06:00 HRS OF 12.03.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 11.03.2018 | CCK | 43170.4312 | 43170.5054 | 1:47 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | FIRE ON POLE | WIRES DAMAGED, SAME REPAIRED | MAIN BAZAR CHANDANI CHOWK-SISGANJ. | 1090
2 | 11.03.2018 | CCK | 43170.462 | 43170.5375 | 1:49 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRES DAMAGED DUE TO FIRE ON POLE | DAMAGED WIRES REPAIRED | MOTHER DAIRY,KAMLA MARKET. | 800
3 | 11.03.2018 | CCK | 43170.4749 | 43170.5243 | 1:11 | LT FEEDER | TO ATTEND FAULT IN THE LINE | JUMPER FOUND BROKEN, SAME REPAIRED | MOSQUE-LAL KUAN BAZAR. | 1237
4 | 11.03.2018 | DRG | 43170.8187 | 43170.8868 | 1:38 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY, AREA BACKFEEDED | DR. AMBEDKAR STADIUM-FEROJ SHAH KOTLA STADIUM. | 44
5 | 11.03.2018 | KRN | 43170.3222 | 43170.3854 | 1:31 | HT SYSTEM FAULT | TRIPPING | RELAY FOUND FAULTY, SAME REPAIRED | JHEEL-JHEEL KHURENJA,BLOCK K-JAGATPURI. | 12800
6 | 11.03.2018 | KRN | 43170.475 | 43170.5361 | 1:28 | HT SYSTEM FAULT | TRIPPING | FUSE BLOWN OF DISTRIBUTION TRANSFORMER DUE TO BIRDAGE, SAME ATTENDED | BLOCK 9-GANDHI NAGAR,SHYAM COLONY. | 3237
7 | 11.03.2018 | KWN | 43170.5194 | 43170.5965 | 1:51 | HVDS CABLE & OTHER SYSTEM | TRIPPING | HVDS CABLE DAMAGED, SAME REPAIRED | NON COMM AREA-SONIA VIHAR EXTENSION. | 345
8 | 11.03.2018 | KWN | 43170.5347 | 43170.5903 | 1:20 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD BURNT, SAME REPAIRED | BLOCK B-KARAWAL NAGAR. | 5611
9 | 11.03.2018 | KWN | 43170.5782 | 43170.6597 | 1:57 | HVDS CABLE & OTHER SYSTEM | HVDS LEAD FAULTY | HVDS LEAD BURNT, SAME REPLACED | JOHRI ENCLAVE-BHAGIRATHI VIHAR. | 25
10 | 11.03.2018 | KWN | 43170.6562 | 43170.7347 | 1:53 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE DAMAGED DUE TO FLASH, SAME REPAIRED | BLOCK D-SHIV VIHAR,KARAWAL NAGAR. | 86
11 | 11.03.2018 | KWN | 43170.6817 | 43170.7299 | 1:09 | HVDS CABLE & OTHER SYSTEM | REPLACEMENT OF HVDS DP FUSE | HVDS DP FUSE BLOWN, SAME REPLACED | BLOCK C-BHAGIRATHI VIHAR. | 1229
12 | 11.03.2018 | NNG | 43170.4236 | 43170.4737 | 1:12 | HT SYSTEM FAULT | TRIPPING | BIRDAGE FOUND ON LINE, SAME ATTENDED | BLOCK D-MEET NAGAR,BLOCK A-EAST GOKUL PURI. | 1488
13 | 11.03.2018 | NNG | 43170.4919 | 43170.5659 | 1:47 | HVDS CABLE & OTHER SYSTEM | TO REPAIR HVDS CABLE | HVDS CABLE FAULTY, SAME REPAIRED | BLOCK D-HARSH VIHAR. | 259
14 | 11.03.2018 | NNG | 43170.5302 | 43170.5983 | 1:38 | HVDS CABLE & OTHER SYSTEM | REPLACEMENT OF HVDS LEAD | HVDS LEAD BURNT, SAME REPAIRED | BLOCK D-MEET NAGAR. | 1488
15 | 11.03.2018 | NNG | 43170.5452 | 43170.6206 | 1:48 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FOUND DAMAGED, SAME REPAIRED | BLOCK B-ANUP VIHAR,SEWA DHAM-MANDOLI. | 173
16 | 11.03.2018 | NNG | 43170.5776 | 43170.6479 | 1:41 | HVDS CABLE & OTHER SYSTEM | TO REPAIR HVDS CABLE | HVDS CABLE FAULTY, SAME REPAIRED | BLOCK C-SEWA DHAM,NAND NAGRI. | 173
17 | 11.03.2018 | NNG | 43170.71 | 43170.7783 | 1:38 | HVDS CABLE & OTHER SYSTEM | HVDS CABLE FAULTY | HVDS CABLE REPAIRED | PRIMARY SCHOOL MEET NAGAR,NAND NAGRI. | 3299
18 | 11.03.2018 | NNG | 43170.8764 | 43170.9271 | 1:13 | HT SYSTEM FAULT | TRIPPING | CONSUMER HT PANEL FLASHED, SAME ATTENDED | JRD HOSPITAL-GTB STAFF COLONY,NAND NAGRI. | 173
19 | 11.03.2018 | YVR | 43170.4581 | 43170.5124 | 1:18 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE BURNT, SAME REPAIRED | BLOCK S-WELCOME COLONY,YAMUNA VIHAR. | 294