## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet3
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 17.03.2018 TO 06:00 HRS OF 18.03.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 17.03.2018 | CCK | 43176.4576 | 43176.6237 | 3:59 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | NAI SARAK-KATRA ASRAFI. | 145 | PREVENTIVE MAINTENANCE CARRIED OUT
2 | 17.03.2018 | DGN | 43176.4375 | 43176.4951 | 1:23 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE DAMAGED DUE TO FLASH, SAME REPAIRED | HANSRAJ SCHOOL-POCKET H,DILSHAD GARDEN. | 8
3 | 17.03.2018 | DGN | 43176.6457 | 43176.708 | 1:30 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE BURNT, SAME REPAIRED | BLOCK J-DILSHAD COLONY. | 169
4 | 17.03.2018 | DGN | 43176.6861 | 43176.7576 | 1:43 | LT FEEDER | TO ATTEND FAULT IN THE LINE | JUMPER FOUND BROKEN, SAME REPLACED | PREM ICE FACTORY. | 22
5 | 17.03.2018 | DRG | 43176.3854 | 43176.4859 | 2:25 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | LT STRAIGHT THROUGH JOINT MADE | EVERGREEN PUBLICATION-KALA MAHAL,DARYAGANJ. | 280 | LT STRAIGHT THROUGH JOINT MADE
6 | 17.03.2018 | DRG | 43176.6447 | 43176.707 | 1:30 | LT FEEDER | TO REPAIR LT CABLE | FAULTY LT CABLE REPAIRED | COMMUNITY CENTRE-JAMA MASZID. | 884
7 | 17.03.2018 | JLM | 43176.4583 | 43176.5826 | 2:59 | PLANNED SHUTDOWN | PROJECT WORK | NEW DISTRIBUTION BOX INSTALLED | EAST ROHTASH NAGAR-SHAHDARA. | 246 | NEW DISTRIBUTION BOX INSTALLED
8 | 17.03.2018 | JLM | 43176.4618 | 43176.5625 | 2:25 | PLANNED SHUTDOWN | TO REPAIR DISTRIBUTION BOX | DISTRIBUTION BOX REPAIRED | KIRAN VIHAR-ANAND VIHAR. | 849 | FAULTY DISTRIBUTION BOX REPAIRED
9 | 17.03.2018 | JLM | 43176.5 | 43176.6451 | 3:29 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | NEW TPD CABLE INSTALLED | J J COLONY-ANAND VIHAR. | 44 | NEW TPD CABLE INSTALLED,TO IMPROVE THE NETWORK
10 | 17.03.2018 | KRN | 43176.4222 | 43176.5347 | 2:42 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK 12-GEETA COLONY,KRISHNA NAGAR. | 448 | PREVENTIVE MAINTENANCE CARRIED OUT
11 | 17.03.2018 | KRN | 43176.4958 | 43176.6148 | 2:51 | PLANNED SHUTDOWN | PROJECT WORK | DT CLEANING WORK CARRIED OUT | KRISHNA NAGAR. | 835 | DT CLEANING WORK CARRIED OUT
12 | 17.03.2018 | KRN | 43176.5147 | 43176.5695 | 1:19 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | TO REPAIR DAMAGED WIRES ON POLE | WIRES DAMAGED DUE TO FIRE ON POLE, SAME REPAIRED | BLOCK F-RAM NAGAR,CHANDER NAGAR. | 750
13 | 17.03.2018 | KRN | 43176.5289 | 43176.5896 | 1:27 | LT FEEDER | TO ATTEND FAULT IN THE LINE | JUMPER FOUND BROKEN, SAME REPLACED | RAM LILA GROUND,KRISHNA NGR. | 964
14 | 17.03.2018 | KRN | 43176.6319 | 43176.6908 | 1:25 | PLANNED SHUTDOWN | PROJECT WORK | DT CLEANING WORK CARRIED OUT | DHRAM PURA-KAILASH NAGAR. | 941
15 | 17.03.2018 | KWN | 43176.4167 | 43176.5761 | 3:50 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | NON COMM AREA-SONIA VIHAR. | 55 | PREVENTIVE MAINTENANCE CARRIED OUT
16 | 17.03.2018 | KWN | 43176.4187 | 43176.6681 | 5:59 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK D-SHIV VIHAR,KARAWAL NAGAR. | 1836 | PREVENTIVE MAINTENANCE CARRIED OUT
17 | 17.03.2018 | KWN | 43176.5025 | 43176.5782 | 1:49 | HVDS CABLE & OTHER SYSTEM | REPLACEMENT OF HVDS LEAD | FAULTY HVDS LEAD REPLACED | BLOCK D-SHIV VIHAR,KARAWAL NAGAR. | 1836
18 | 17.03.2018 | KWN | 43176.5563 | 43176.6358 | 1:55 | HVDS CABLE & OTHER SYSTEM | REPLACEMENT OF HTAB LEAD | HTAB LEAD FAULTY, SAME REPLACED | NON COMM AREA-SONIA VIHAR. | 86
19 | 17.03.2018 | KWN | 43176.5903 | 43176.641 | 1:13 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | BIRDAGE FOUND ON LINE, SAME ATTENDED | BLOCK N-SHIV VIHAR,SONIA VIHAR. | 5040
20 | 17.03.2018 | LNR | 43176.4347 | 43176.6659 | 5:33 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | POLICE QUARTERS,LAXMI NAGAR. | 3912 | PREVENTIVE MAINTENANCE CARRIED OUT
21 | 17.03.2018 | LNR | 43176.4437 | 43176.6539 | 5:03 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK F VINOD NAGAR WEST-MOTHER DAIRY. | 173 | PREVENTIVE MAINTENANCE CARRIED OUT
22 | 17.03.2018 | LNR | 43176.4472 | 43176.714 | 6:24 | PLANNED SHUTDOWN | PROJECT WORK | NEW LTAB LAID | BLOCK D-PREET VIHAR. | 55 | NEW LTAB LAID TO IMPROVE THE NETWORK
23 | 17.03.2018 | LNR | 43176.4752 | 43176.556 | 1:56 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE BURNT, SAME REPAIRED | BLOCK U-CHANDER VIHAR,LAXMI NGR. | 130
24 | 17.03.2018 | LNR | 43176.4965 | 43176.5748 | 1:53 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | REPLACEMENT OF LT ACB | FAULTY LT ACB REPLACED | BLOCK C-LALITA PARK,LAXMI NGR. | 747
25 | 17.03.2018 | LNR | 43176.6333 | 43176.6876 | 1:18 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE DAMAGED DUE TO FLASH, SAME REPAIRED | BLOCK J & K-NARAYAN NAGAR. | 747
26 | 17.03.2018 | LNR | 43176.802 | 43176.8696 | 1:37 | LT FEEDER | LT CABLE DAMAGED DUE TO FIRE ON POLE | LT CABLE REPAIRED | MANDAWALI,LAXMI NAGAR. | 2023
27 | 17.03.2018 | MVR | 43176.5069 | 43176.622 | 2:46 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CL-CHILLA SARDA BANGAR VILLAGE,MVR. | 586 | PREVENTIVE MAINTENANCE CARRIED OUT
28 | 17.03.2018 | MVR | 43176.5208 | 43176.7381 | 5:13 | PLANNED SHUTDOWN | PROJECT WORK | DT CLEANING WORK CARRIED OUT | BLOCK 17-KALYAN PURI. | 86 | DT CLEANING WORK CARRIED OUT
29 | 17.03.2018 | NNG | 43176.3976 | 43176.4745 | 1:51 | HT SYSTEM FAULT | TRIPPING | HTAB DAMAGED ,SAME REPAIRED | BLOCK D-MEET NAGAR,BLOCK A-EAST GOKUL PURI. | 1530
30 | 17.03.2018 | NNG | 43176.398 | 43176.4792 | 1:57 | HT SYSTEM FAULT | TO REPAIR HTAB CABLE | FAULTY HTAB REPAIRED | BLOCK A-ANUP VIHAR. | 3341
31 | 17.03.2018 | NNG | 43176.4319 | 43176.5909 | 3:49 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK B-KABIR NAGAR,NAND NAGRI. | 568 | PREVENTIVE MAINTENANCE CARRIED OUT
32 | 17.03.2018 | NNG | 43176.434 | 43176.6876 | 6:05 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK D-HARSH VIHAR. | 216 | PREVENTIVE MAINTENANCE CARRIED OUT
33 | 17.03.2018 | NNG | 43176.5632 | 43176.6415 | 1:53 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | BLOCK B-SUNDER NAGRI NNG. | 13367
34 | 17.03.2018 | NNG | 43176.7088 | 43176.7755 | 1:36 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY, SAME REPAIRED | NEW MANDOLI INDUSTRIAL AREA. | 173
35 | 17.03.2018 | NNG | 43176.8143 | 43176.8771 | 1:30 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT SOCKET DAMAGED, SAME REPAIRED | BLOCK A-EAST GOKUL PURI. | 2074
36 | 17.03.2018 | PHG | 43176.4264 | 43176.6539 | 5:28 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CHOWK NAI BASTI-SADAR BAZAR. | 1188 | PREVENTIVE MAINTENANCE CARRIED OUT
37 | 17.03.2018 | PHG | 43176.5056 | 43176.6011 | 2:18 | PLANNED SHUTDOWN | TO REPLACE THE PIERCING CONNECTOR | PIERCING CONNECTOR REPLACED | A.B. PATRIKA,KAMLA MARKET. | 41 | PIERCING CONNECTOR REPLACED
38 | 17.03.2018 | PNR | 43176.4215 | 43176.5881 | 4:00 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | VIKRANT TOWER,PATEL NAGAR. | 155 | PREVENTIVE MAINTENANCE CARRIED OUT
39 | 17.03.2018 | PNR | 43176.5889 | 43176.6411 | 1:15 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | LT CIRCUIT MAINTENANCE WORK CARRIED OUT | BLOCK T-PANJABI BASTI. | 276
40 | 17.03.2018 | PNR | 43176.5889 | 43176.6408 | 1:15 | PLANNED SHUTDOWN | PROJECT WORK | LT CABLE REPAIRED | BLOCK T-BALJIT NAGAR. | 274
41 | 17.03.2018 | PNR | 43176.5889 | 43176.6413 | 1:15 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | DISTRIBUTION BOX REPAIRED | BLOCK T-BALJIT NAGAR. | 84
42 | 17.03.2018 | PNR | 43176.5889 | 43176.7007 | 2:41 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | NEW CABLE LAID | BLOCK T-WEST PATEL NAGAR. | 510 | NEW CABLE LAID TO INCREASE THE NETWORK CAPACITY
43 | 17.03.2018 | SRD | 43176.4479 | 43176.5694 | 2:55 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK_1A-REHAGAR PURA. | 1059 | PREVENTIVE MAINTENANCE CARRIED OUT
44 | 17.03.2018 | VSE | 43176.4931 | 43176.5986 | 2:32 | PLANNED SHUTDOWN | REPLACEMENT OF DISTRIBUTION BOX | FAULTY DISTRIBUTION BOX REPLACED | BLOCK B-DALLU PURA VSE. | 349 | FAULTY DISTRIBUTION BOX REPLACED
45 | 17.03.2018 | VSE | 43176.5166 | 43176.5938 | 1:51 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND BROKEN SAME ATTENDED | KONDALI VILLAGE-GHAROLI KONDLI. | 983
46 | 17.03.2018 | YVR | 43176.4193 | 43176.4749 | 1:20 | HT SYSTEM FAULT | LOAD UNBALANCED | LOAD BALANCING CARRIED OUT | BLOCK P-BRAHM PURI,BLOCK B-MANUJPUR. | 1675
47 | 17.03.2018 | YVR | 43176.4507 | 43176.5443 | 2:15 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK I-BRAHM PURI,GHONDA PATTI CHAUHAN. | 1073 | PREVENTIVE MAINTENANCE CARRIED OUT
48 | 17.03.2018 | YVR | 43176.4509 | 43176.5283 | 1:51 | DISTRIBUTION TR. | MAINTENANCE OF TRANSFORMER | TRANSFORMER MAINTENANCE WORK CARRIED OUT | BLOCK M-BRAHM PURI,BLOCK K-BRAHM PURI. | 2577
49 | 17.03.2018 | YVR | 43176.4569 | 43176.5655 | 2:36 | PLANNED SHUTDOWN | NETWORK UPGRADATION WORK | DISTRIBUTION BOX REPAIRED | BLOCK V-GHONDA PATTI CHAUHAN. | 639 | FAULTY DISTRIBUTION BOX REPAIRED
50 | 17.03.2018 | YVR | 43176.4627 | 43176.5278 | 1:34 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRES DAMAGED DUE TO FIRE ON POLE | DAMAGED WIRE'S REPAIRED | BLOCK A-SHASTRI PARK. | 259
51 | 17.03.2018 | YVR | 43176.4667 | 43176.5658 | 2:23 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE | MAUJPUR,YAMUNA VIHAR. | 1546 | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE
52 | 17.03.2018 | YVR | 43176.4689 | 43176.5694 | 2:25 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | CABLE END BOX FAULTY, SAME REPAIRED | BLOCK C1,C9-YAMUNA VIHAR. | 1723 | FAULTY CABLE END BOX REPAIRED
53 | 17.03.2018 | YVR | 43176.4733 | 43176.5434 | 1:41 | HT SYSTEM FAULT | TO ATTEND HOT POINTS IN THE NETWORK | HOT POINTS ATTENDED IN THE NETWORK | BLOCK C-SHASTRI PARK. | 86
54 | 17.03.2018 | YVR | 43176.4799 | 43176.5456 | 1:35 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LTAB DAMAGED DUE TO FLASH, SAME REPAIRED | BLOCK F-BRAHM PURI,YAMUNA VIHAR. | 3004
55 | 17.03.2018 | YVR | 43176.4847 | 43176.6665 | 4:22 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE | JAFFRABAD-MAUJ PUR. | 2609 | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE
56 | 17.03.2018 | YVR | 43176.4938 | 43176.6681 | 4:11 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK C-NEW SEELAMPUR PHASE IV. | 569 | PREVENTIVE MAINTENANCE CARRIED OUT
57 | 17.03.2018 | YVR | 43176.5208 | 43176.6089 | 2:07 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | REPLACEMENT OF LT ACB | FAULTY LT ACB REPLACED | BLOCK P-BRAHM PURI,BLOCK B-MANUJPUR. | 1675 | FAULTY LT ACB REPLACED
58 | 17.03.2018 | YVR | 43176.5389 | 43176.6264 | 2:06 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE | JAFFRABAD-MAUJ PUR. | 3783 | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE
59 | 17.03.2018 | YVR | 43176.5715 | 43176.6261 | 1:19 | PLANNED SHUTDOWN | PROJECT WORK | LT NETWORK REPAIRED | ARVIND NAGAR-GHONDA. | 1279
60 | 17.03.2018 | YVR | 43176.6236 | 43176.6787 | 1:19 | PLANNED SHUTDOWN | PROJECT WORK | LT NETWORK REPAIRED | SUBHASH PARK-GORAKH PARK. | 1233
61 | 17.03.2018 | YVR | 43176.6333 | 43176.7241 | 2:11 | PLANNED SHUTDOWN | PROJECT WORK | LT CIRCUIT MAINTENANCE WORK CARRIED OUT | GHONDA PATTI CHAUHAN,BLOCK I-BRAHM PURI. | 965 | LT CIRCUIT MAINTENANCE WORK CARRIED OUT
62 | 17.03.2018 | YVR | 43176.6479 | 43176.7243 | 1:50 | PLANNED SHUTDOWN | PROJECT WORK | DISTRIBUTION BOX REPAIRED & LT STRAIGHT THROUGH JOINT MADE | JANTA COLONY,YAMUNA VIHAR. | 325
63 | 17.03.2018 | YVR | 43176.6479 | 43176.7296 | 1:58 | PLANNED SHUTDOWN | PROJECT WORK | LT CIRCUIT MAINTENANCE WORK CARRIED OUT | BLOCK E-ZERO PUSTA. | 1748
64 | 17.03.2018 | YVR | 43176.6486 | 43176.7294 | 1:56 | PLANNED SHUTDOWN | PROJECT WORK | LT CIRCUIT MAINTENANCE WORK CARRIED OUT | BLOCK J-SEELAMPUR COLONY. | 184
65 | 17.03.2018 | YVR | 43176.8034 | 43176.8773 | 1:46 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | FIRE ON LT POLE | LT CABLE BURNT, SAME REPAIRED | BLOCK B-GARI MANDU,BLOCK B-MANUJPUR. | 87