## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet3
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 20.03.2018 TO 06:00 HRS OF 21.03.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 20.03.2018 | CCK | 43179.425 | 43179.5757 | 3:37 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | NAI SARAK-KATRA ASRAFI | 730 | PREVENTIVE MAINTENANCE CARRIED OUT
2 | 20.03.2018 | DGN | 43179.3543 | 43179.7778 | 10:10 | HT SYSTEM FAULT | HT PANEL FAULTY | HT PANEL REPLACED BY NEW ONE | LIG FLATS-POCKET F & E G T ROAD | 2078 | PANEL FAULTY SAME REPLACED BY NEW ONE
3 | 20.03.2018 | DGN | 43179.4583 | 43179.6436 | 4:27 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK A-JHILMIL INDUSTRIAL AREA | 378 | PREVENTIVE MAINTENANCE CARRIED OUT
4 | 20.03.2018 | DGN | 43179.4931 | 43179.6513 | 3:48 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | JHILMIL INDUSTRIAL AREA-JHILMIL COLONY | 38 | PREVENTIVE MAINTENANCE CARRIED OUT
5 | 20.03.2018 | DGN | 43179.5167 | 43179.5931 | 1:50 | LT FEEDER | REPLACEMENT OF PIERCING CONNECTOR | PIERCING CONNECTOR REPLACED | L & H-POCKET DILSHAD GARDEN | 48
6 | 20.03.2018 | DGN | 43179.6881 | 43179.7441 | 1:21 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | DAMODAR PARK G T ROAD | 305
7 | 20.03.2018 | DGN | 43179.7138 | 43180.0605 | 8:19 | DAMAGE BY OTHER AGENCIES | POLE DAMAGED BY UNKNOWN VEHICLE | DAMAGED POLE REPLACED BY NEW ONE | B BLOCK-JHILMIL INDUSTRIAL AREA | 29 | POLE DAMAGED BY UNKNOWN VEHICLE. NEW POLE INSTALLED
8 | 20.03.2018 | DRG | 43179.3993 | 43179.4814 | 1:58 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CHRISTAN COLONY-KHABAS PURA | 280
9 | 20.03.2018 | DRG | 43179.4896 | 43179.571 | 1:57 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT SOCKET DAMAGED SAME REPLACED | DDA FLATS-KALA MASZID | 318
10 | 20.03.2018 | DRG | 43179.8032 | 43179.8646 | 1:28 | HT SYSTEM FAULT | TRIPPING | TRANSIENT FAULT | DEMOLISHED AREA-ROUSE AVENUE | 397
11 | 20.03.2018 | JLM | 43179.4236 | 43179.5486 | 3:00 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | GOVIND KHAND-JHILMIL COLONY | 986 | PREVENTIVE MAINTENANCE CARRIED OUT
12 | 20.03.2018 | JLM | 43179.4444 | 43179.5208 | 1:50 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | EAST ROHTASH NAGAR-SHAHDARA | 87
13 | 20.03.2018 | JLM | 43179.4722 | 43179.5972 | 3:00 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | KIRAN VIHAR-ANAND VIHAR | 849 | PREVENTIVE MAINTENANCE CARRIED OUT
14 | 20.03.2018 | JLM | 43179.5556 | 43179.6389 | 2:00 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | B-BLOCK VIVEK VIHAR | 600 | PREVENTIVE MAINTENANCE CARRIED OUT
15 | 20.03.2018 | KRN | 43179.3948 | 43179.4444 | 1:11 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | BLOCK K-JAGATPURI | 12815
16 | 20.03.2018 | KRN | 43179.4278 | 43179.5629 | 3:15 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | GOVIND PURA OLD-SWASTHYA VIHAR | 921 | PREVENTIVE MAINTENANCE CARRIED OUT
17 | 20.03.2018 | KRN | 43179.4604 | 43179.6245 | 3:56 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | RAGHUBARPURA NO 2-SEELAMPUR | 85 | PREVENTIVE MAINTENANCE CARRIED OUT
18 | 20.03.2018 | KRN | 43179.4736 | 43179.581 | 2:35 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK F-CHANDAR NAGAR | 974 | PREVENTIVE MAINTENANCE CARRIED OUT
19 | 20.03.2018 | KRN | 43179.5292 | 43179.684 | 3:43 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | OLD SEELAMPUR DHRAM PURA | 1102 | PREVENTIVE MAINTENANCE CARRIED OUT
20 | 20.03.2018 | KRN | 43179.7292 | 43179.7827 | 1:17 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | BLOCK X-RAJGARH COLONY | 141
21 | 21.03.2018 | KRN | 43180.0448 | 43180.0873 | 1:01 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | BLOCK C-KANTI NAGAR NORTH | 490
22 | 20.03.2018 | KWN | 43179.4132 | 43179.4743 | 1:28 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK CN-AMBIKA VIHAR | 92
23 | 20.03.2018 | KWN | 43179.4201 | 43179.5854 | 3:58 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | VILLAGE-KAMAL VIHAR | 130 | PREVENTIVE MAINTENANCE CARRIED OUT
24 | 20.03.2018 | KWN | 43179.4208 | 43179.6687 | 5:57 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK U-SHIV VIHAR | 2966 | PREVENTIVE MAINTENANCE CARRIED OUT
25 | 20.03.2018 | KWN | 43179.5605 | 43179.6438 | 2:00 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | BHAGIRATHI VIHAR | 484
26 | 20.03.2018 | LNR | 43179.4736 | 43179.5608 | 2:06 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | NAVA KUNJ APARTMENT-MOTHER DAIRY | 130 | PREVENTIVE MAINTENANCE CARRIED OUT
27 | 20.03.2018 | LNR | 43179.5333 | 43179.7161 | 4:23 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK WA&O-SHAKARPUR KHAS | 1517 | PREVENTIVE MAINTENANCE CARRIED OUT
28 | 20.03.2018 | LNR | 43179.7394 | 43179.8147 | 1:48 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT MAIN FLASHED SAME ATTENDED | BLOCK G-PREET VIHAR | 85
29 | 20.03.2018 | MVR | 43179.489 | 43179.5536 | 1:33 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | PKT B-MAYUR VIHAR PHASE II | 247
30 | 20.03.2018 | MVR | 43179.5504 | 43179.6202 | 1:41 | HT SYSTEM FAULT | TRIPPING | MECHANISM OF BREAKER FAULTY SAME REPAIRED | ACHARYA NIKETAN-SHASHI GARDEN | 4212
31 | 20.03.2018 | NNG | 43179.4201 | 43179.4962 | 1:50 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BHARAT MATA MANDIR-JJ COLONY | 432
32 | 20.03.2018 | NNG | 43179.4417 | 43179.7083 | 6:24 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | SABOLI COLONY-MANDOLI | 148 | PREVENTIVE MAINTENANCE CARRIED OUT
33 | 20.03.2018 | NNG | 43179.4417 | 43179.5903 | 3:34 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK E-SEWA DHAM | 263 | PREVENTIVE MAINTENANCE CARRIED OUT
34 | 20.03.2018 | NNG | 43179.5446 | 43179.6042 | 1:26 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK D-MEET NAGAR | 1530
35 | 20.03.2018 | NNG | 43179.5689 | 43179.6343 | 1:34 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LTAB FAULTY SAME REPAIRED | CHHAJJUPUR-BABAR PUR | 3652
36 | 20.03.2018 | NNG | 43179.6194 | 43179.6954 | 1:50 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK D-HARSH VIHAR | 432
37 | 20.03.2018 | NNG | 43179.6271 | 43179.6875 | 1:27 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | BLOCK B-EAST GOKUL PURI | 1530
38 | 20.03.2018 | NNG | 43179.6381 | 43179.6875 | 1:11 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT SOCKET DAMAGED SAME REPLACED | BLOCK F-DURGA PURI | 432
39 | 20.03.2018 | PHG | 43179.4257 | 43179.6581 | 5:35 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | HATHI KHANA-NAWAB GANJ | 1431 | PREVENTIVE MAINTENANCE CARRIED OUT
40 | 20.03.2018 | SRD | 43179.4583 | 43179.5799 | 2:55 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | PART I- BLOCK R-NEW RAJENDRA NAGAR | 101 | PREVENTIVE MAINTENANCE CARRIED OUT
41 | 20.03.2018 | YVR | 43179.4306 | 43179.6939 | 6:19 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | JAFFRABAD-MAUJ PUR | 2609 | PREVENTIVE MAINTENANCE CARRIED OUT
42 | 20.03.2018 | YVR | 43179.45 | 43179.6632 | 5:07 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK C-BHAJANPURA | 5800 | PREVENTIVE MAINTENANCE CARRIED OUT
43 | 20.03.2018 | YVR | 43179.4632 | 43179.6246 | 3:52 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | YAMUNA FLOOD PLAINS-YVR | 139 | PREVENTIVE MAINTENANCE CARRIED OUT
44 | 20.03.2018 | YVR | 43179.4688 | 43179.5854 | 2:48 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK U-WELCOME COLONY | 2661 | PREVENTIVE MAINTENANCE CARRIED OUT
45 | 20.03.2018 | YVR | 43179.4944 | 43179.5381 | 1:03 | HT SYSTEM FAULT | FOR REMOVING ILLEGAL TAPPING | ILLEGAL TAPPING REMOVED | BLOCK A-SILAMPUR COLONY | 167
46 | 20.03.2018 | YVR | 43179.4997 | 43179.5492 | 1:11 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | JAG JEEVAN NAGAR-NEW KATWARA | 837
47 | 20.03.2018 | YVR | 43179.5312 | 43179.5967 | 1:34 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CHAUHAN BANGAR-JAFFRABAD | 3783
48 | 20.03.2018 | YVR | 43179.5965 | 43179.7201 | 2:58 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | JANTA COLONY YVR | 1056 | PREVENTIVE MAINTENANCE CARRIED OUT
49 | 20.03.2018 | YVR | 43179.5972 | 43179.725 | 3:04 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK C-NEW SILAMPURI PHASE IV | 569 | PREVENTIVE MAINTENANCE CARRIED OUT
50 | 20.03.2018 | YVR | 43179.5972 | 43179.7247 | 3:04 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK C-GHONDA PATTI | 1245 | PREVENTIVE MAINTENANCE CARRIED OUT
51 | 20.03.2018 | YVR | 43179.625 | 43179.6769 | 1:15 | HT SYSTEM FAULT | FIRE IN LTAB | LTAB REPAIRED | MAUJPUR VILLAGE | 2448
52 | 20.03.2018 | YVR | 43179.6424 | 43179.7253 | 1:59 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK A-GARI MANDU-YVR | 1670
53 | 20.03.2018 | YVR | 43179.6426 | 43179.692 | 1:11 | HT SYSTEM FAULT | FIRE IN LTAB | LTAB REPAIRED | TIKONA PARK YAMUNA VIHAR | 2018
54 | 20.03.2018 | YVR | 43179.6727 | 43179.7393 | 1:36 | DISTRIBUTION TR. | NETWORK UPGRADATION | INSTALLATION OF ADDITIONAL TRANSFORMER | BLOCK E-SUBHASH MOHALLA | 1157
55 | 20.03.2018 | YVR | 43179.7625 | 43179.825 | 1:30 | HT SYSTEM FAULT | TRIPPING | TRANSIENT FAULT | DELHI VIDHYUT BROAD-ZERO PUSTA | 305