## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## Sheet3
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 21.03.2018 TO 06:00 HRS OF 22.03.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 21.03.2018 | CCK | 43180.45 | 43180.5855 | 3:15 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | MAIN BAZAR-KHUSH DIL | 1526 | PREVENTIVE MAINTENANCE CARRIED OUT
2 | 21.03.2018 | CCK | 43180.4604 | 43180.5372 | 1:50 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRE DAMAGED DUE TO FLASH ON POLE | DAMAGED WIRE REPAIRED | NAYA BAZAR-CHANDNI CHOWK | 269
3 | 21.03.2018 | DGN | 43180.4432 | 43180.5188 | 1:49 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | POCKET H-DILSHAD GARDEN | 14
4 | 21.03.2018 | DGN | 43180.4549 | 43180.5882 | 3:12 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK J & K- DILSHAD GARDEN | 545 | PREVENTIVE MAINTENANCE CARRIED OUT
5 | 21.03.2018 | DGN | 43180.4549 | 43180.5354 | 1:56 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | BLOCK G-OLD SIMAPURI | 154
6 | 21.03.2018 | DGN | 43180.47 | 43180.5472 | 1:51 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | BLOCK D-JHILMIL INDUSTRIAL AREA | 164
7 | 21.03.2018 | DGN | 43180.5132 | 43180.5759 | 1:30 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | DP FUSE BLOWN SAME REPLACED | OLDANPUR-NAVIN SHAHDARA | 562
8 | 21.03.2018 | DGN | 43180.5174 | 43180.7195 | 4:51 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | RAJIV COLONY-JHILMIL INDUSTRIAL AREA | 101 | PREVENTIVE MAINTENANCE CARRIED OUT
9 | 21.03.2018 | DGN | 43180.5521 | 43180.6319 | 1:55 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT JUMPER FOUND LOOSE SAME ATTENDED | MCD COLONY -OLD SIMAPURI | 40
10 | 21.03.2018 | DGN | 43180.9829 | 43181.0338 | 1:13 | LT FEEDER | TO ATTEND FAULT IN THE LINE | EXTERNAL ELEMENT FOUND ON LINE SAME REMOVED | B-BLOCK DILSHAD GARDEN | 68
11 | 21.03.2018 | DRG | 43180.445 | 43180.5217 | 1:50 | LT FEEDER | LTAB CONDUCTOR DAMAGED | LTAB CONDUCTOR REPAIRED | HINDI PARK DARYA GANJ | 110
12 | 21.03.2018 | DRG | 43180.4917 | 43180.5659 | 1:47 | LT FEEDER | LTAB CONDUCTOR DAMAGED | LTAB CONDUCTOR REPAIRED | PART OF DARYA GANJ | 110
13 | 21.03.2018 | DRG | 43180.5347 | 43180.5973 | 1:30 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | COMMUNITY CENTRE-JAMA MASZID | 427
14 | 21.03.2018 | JLM | 43180.4201 | 43180.5417 | 2:55 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | VISHWAS NAGAR-SHAHDARA | 344 | PREVENTIVE MAINTENANCE CARRIED OUT
15 | 21.03.2018 | JLM | 43180.5556 | 43180.6806 | 3:00 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | J J COLONY-ANAND VIHAR | 45 | PREVENTIVE MAINTENANCE CARRIED OUT
16 | 21.03.2018 | JLM | 43180.5625 | 43180.7198 | 3:47 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | MANAK VIHAR-ANAND VIHAR | 185 | PREVENTIVE MAINTENANCE CARRIED OUT
17 | 21.03.2018 | KRN | 43180.4368 | 43180.5312 | 2:16 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | E-BLOCK KRISHNA NAGAR | 1202 | PREVENTIVE MAINTENANCE CARRIED OUT
18 | 21.03.2018 | KRN | 43180.45 | 43180.7229 | 6:33 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CHANDER NAGAR-KRISHNA NAGAR | 3640 | PREVENTIVE MAINTENANCE CARRIED OUT
19 | 21.03.2018 | KRN | 43180.4861 | 43180.6403 | 3:42 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BALDEV PARK-JAGATPURI | 1362 | PREVENTIVE MAINTENANCE CARRIED OUT
20 | 21.03.2018 | KRN | 43180.5097 | 43180.5856 | 1:49 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | GANDHI NAGAR-KAILASH NAGAR | 765
21 | 21.03.2018 | KRN | 43180.6 | 43180.6607 | 1:27 | HT SYSTEM FAULT | HTAB CONDUCTOR BURNT | HTAB CONDUCTOR REPAIRED | CHAND MOHALLA-RAJGARH COLONY | 1424
22 | 21.03.2018 | KWN | 43180.4201 | 43180.6458 | 5:25 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK O & P SHIV VIHAR KARWAL NAGAR | 170 | PREVENTIVE MAINTENANCE CARRIED OUT
23 | 21.03.2018 | KWN | 43180.438 | 43180.5174 | 1:54 | DISTRIBUTION TR. | OIL LEAKAGE FROM TRANSFORMER BUSHING | OIL LEAKAGE PROBLEM ATTENDED | BLOCK P-SHIV VIHAR | 88
24 | 21.03.2018 | KWN | 43180.4479 | 43180.5722 | 2:59 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BHAGAT NAGAR-DAYALPUR | 1250 | PREVENTIVE MAINTENANCE CARRIED OUT
25 | 21.03.2018 | KWN | 43180.5417 | 43180.7292 | 4:30 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BHAJANPURA-DAYALPUR | 1352 | PREVENTIVE MAINTENANCE CARRIED OUT
26 | 21.03.2018 | KWN | 43180.6273 | 43180.7035 | 1:50 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | GALI NO-1 TUNDA NAGAR | 149
27 | 21.03.2018 | KWN | 43180.6327 | 43180.7125 | 1:55 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | GALI NO-3 PHASE-1 SHIV VIHAR | 345
28 | 21.03.2018 | KWN | 43180.6441 | 43180.6875 | 1:02 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | LIG DDA FLATS-SONIA VIHAR | 1600
29 | 21.03.2018 | KWN | 43180.6499 | 43180.7249 | 1:48 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | FAULT IN LT ACB | ACB REPLACED | BLOCK K-WEST KARAWAL NAGAR | 326
30 | 21.03.2018 | LNR | 43180.4583 | 43180.7356 | 6:39 | PLANNED SHUTDOWN | NEW LTAB CIRCUIT LAYING | NEW LTAB CIRCUIT LAID | BLOCK D-PREET VIHAR | 55 | NEW LTAB CIRCUIT LAYING WORK
31 | 21.03.2018 | LNR | 43180.5 | 43180.7038 | 4:54 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK A-GURU RAMDAS NAGAR | 228 | PREVENTIVE MAINTENANCE CARRIED OUT
32 | 21.03.2018 | LNR | 43180.5639 | 43180.6685 | 2:31 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK B-VINOD NAGAR EAST | 2089 | PREVENTIVE MAINTENANCE CARRIED OUT
33 | 21.03.2018 | LNR | 43180.5743 | 43180.6987 | 2:59 | DISTRIBUTION TR. | TRANSFORMER REPLACEMENT UNDER LOW IR VALUE | TRANSFORMER REPLACED WITH MOBILE TRANSFORMER | SPS BLOCK DDA PARK LAXMI NAGAR | 1896 | TRANSFORMER REPLACED WITH MOBILE TRANSFORMER
34 | 21.03.2018 | NNG | 43180.4174 | 43180.4882 | 1:42 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | SABOLI COLONY-MANDOLI | 124
35 | 21.03.2018 | NNG | 43180.4177 | 43180.4951 | 1:51 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | NEW MANDOLI INDUSTRIAL AREA | 250
36 | 21.03.2018 | NNG | 43180.4223 | 43180.5021 | 1:55 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | BLOCK D-MEET NAGAR | 1530
37 | 21.03.2018 | NNG | 43180.4313 | 43180.5472 | 2:47 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK D-JYOTI NAGAR | 475 | PREVENTIVE MAINTENANCE CARRIED OUT
38 | 21.03.2018 | NNG | 43180.4436 | 43180.5243 | 1:56 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS DP FUSE BLOWN SAME REPLACED | BLOCK D-HARSH VIHAR | 430
39 | 21.03.2018 | NNG | 43180.4475 | 43180.5229 | 1:49 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | HARSH VIHAR SUB STATION-POLICE FARM | 254
40 | 21.03.2018 | NNG | 43180.4684 | 43180.5423 | 1:46 | LT FEEDER | TO ATTEND FAULT IN THE LINE | DISTRIBUTION BOX FAULTY SAME REPAIRED | BLOCK C-KABIR NAGAR | 1207
41 | 21.03.2018 | NNG | 43180.5299 | 43180.6863 | 3:45 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BUDH VIHAR-SEWA DHAM | 216 | PREVENTIVE MAINTENANCE CARRIED OUT
42 | 21.03.2018 | NNG | 43180.5442 | 43180.6132 | 1:39 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | LT SOCKET DAMAGED SAME REPLACED | PKT B-CHITRAKOOT | 6422
43 | 21.03.2018 | NNG | 43180.6551 | 43180.7361 | 1:57 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY SAME REPAIRED | BLOCK A-EAST GOKUL PURI | 1530
44 | 21.03.2018 | NNG | 43180.6653 | 43180.7431 | 1:52 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK A-MANDOLI EXTENSION | 215
45 | 21.03.2018 | NNG | 43180.6658 | 43180.7431 | 1:51 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK D-HARSH VIHAR | 124
46 | 21.03.2018 | NNG | 43180.6733 | 43180.7521 | 1:53 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | BLOCK A-ANUP VIHAR | 3341
47 | 21.03.2018 | NNG | 43180.7423 | 43180.8023 | 1:26 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | SABOLI VILLAGE-MANDOLI | 124
48 | 21.03.2018 | PHG | 43180.425 | 43180.678 | 6:04 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK T-AHATA KEDARA | 125 | PREVENTIVE MAINTENANCE CARRIED OUT
49 | 21.03.2018 | PNR | 43180.4708 | 43180.5511 | 1:56 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK R-BALJIT NAGAR | 190
50 | 21.03.2018 | PNR | 43180.4708 | 43180.5509 | 1:55 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK V-WEST PATEL NAGAR | 57
51 | 21.03.2018 | PNR | 43180.4708 | 43180.5508 | 1:55 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | DHEERAJ PAHADI ANAND PARVAT | 361
52 | 21.03.2018 | PNR | 43180.6562 | 43180.7239 | 1:37 | HT SYSTEM FAULT | FAULT IN LT ACB | LT ACB REPLACEMENT | BLOCK-5B-DEV NAGAR | 1521
53 | 21.03.2018 | SRD | 43180.4067 | 43180.4604 | 1:17 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | TO ATTEND FAULT IN THE LINE | DISTRIBUTION BOX FAULTY SAME REPAIRED | BLOCK 16-OLD RAJENDRA NAGAR | 327
54 | 21.03.2018 | SRD | 43180.4514 | 43180.5746 | 2:57 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK-24N-BEADON PURA | 410 | PREVENTIVE MAINTENANCE CARRIED OUT
55 | 21.03.2018 | SRD | 43180.5347 | 43180.6434 | 2:36 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | CENTRAL RIDGE RESERVED FOREST AREA | 327 | PREVENTIVE MAINTENANCE CARRIED OUT
56 | 21.03.2018 | SRD | 43180.6844 | 43180.7649 | 1:56 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY AREA BACKFEEDED | AJMAL KHAN PARK SRD-KAROL BAGH | 185
57 | 21.03.2018 | YVR | 43180.3798 | 43180.4417 | 1:29 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | SOCKET BURNT SAME REPLACED | VIJAY PARK-YAMUNA VIHAR | 3478
58 | 21.03.2018 | YVR | 43180.4619 | 43180.5376 | 1:49 | LT FEEDER | FOR REMOVING ILLEGAL TAPPING | ILLEGAL TAPPING REMOVED | BLOCK D-MAUJ PUR | 82
59 | 21.03.2018 | YVR | 43180.4674 | 43180.6401 | 4:09 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | GHONDA PATTI CHAUHAN | 965 | PREVENTIVE MAINTENANCE CARRIED OUT
60 | 21.03.2018 | YVR | 43180.4792 | 43180.5905 | 2:40 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK C-12-SONIA VIHAR, | 1527 | PREVENTIVE MAINTENANCE CARRIED OUT
61 | 21.03.2018 | YVR | 43180.5694 | 43180.7122 | 3:26 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK C-NEW SILAMPURI PHASE IV | 569 | PREVENTIVE MAINTENANCE CARRIED OUT
62 | 21.03.2018 | YVR | 43180.5694 | 43180.712 | 3:25 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | JANTA COLONY DWARKAPURI | 278 | PREVENTIVE MAINTENANCE CARRIED OUT
63 | 21.03.2018 | YVR | 43180.591 | 43180.7125 | 2:55 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK V-GHONDA PATTI CHAUHAN | 639 | PREVENTIVE MAINTENANCE CARRIED OUT
64 | 21.03.2018 | YVR | 43180.5924 | 43180.7165 | 2:59 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE CARRIED OUT | 3RD PUSHTA-SONIA VIHAR | 1546 | PREVENTIVE MAINTENANCE CARRIED OUT