## Sheet1 (hidden)
DAMAGE BY OTHER AGENCIES
DISTRIBUTION TR.
FORCE MAJEURE (RAIN/WATER LOGGING/STORM, ETC.)
HT SYSTEM FAULT
HVDS CABLE & OTHER SYSTEM
HVDS TRANSFORMER
LT SYSTEM FEEDER PILLAR, TERMINATION, ETC.
LT FEEDER
PLANNED SHUTDOWN
SHEDDING TO REDUCE OVERDRAWAL
TRANSMISSION SYSTEM DTL/PGCIL

## OUTAGE
DISCOM : BYPL
OUTAGE REPORT FOR:06:00HRS. OF 31.03.2018 TO 06:00 HRS OF 01.04.2018
Sr. No. | Date | Division | Start Time | End Time | Duration | Reason for Outage |  | Action | Main Area affected | No. of consumer affected | Remarks
Details
1 | 31.03.2018 | CCK | 43190.4971 | 43190.561 | 1:32 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | REPLACEMENT OF SOCKET | DAMAGED SOCKET REPLACED | BALI MARAN-BARA DARI,MOSQUE-LAL KUAN BAZAR. | 774
2 | 31.03.2018 | CCK | 43190.4979 | 43190.5555 | 1:23 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | BELA ROAD,CHANDNI CHOWK. | 154
3 | 31.03.2018 | DGN | 43190.4319 | 43190.5222 | 2:10 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | GOVT SCHOOL NO-2-DDA FLATS,DILSHAD GARDEN. | 247 | PREVENTIVE MAINTENANCE CARRIED OUT
4 | 31.03.2018 | DRG | 43190.4763 | 43190.5204 | 1:03 | LT FEEDER | TO ATTEND FAULT IN THE LINE | LT CABLE DAMAGED, SAME REPAIRED | SHEESH MAHAL,GB PANT. | 1914
5 | 31.03.2018 | JLM | 43190.4583 | 43190.5035 | 1:05 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | KARKARDOOMA COMPLAX-KARKAR DUMA. | 82
6 | 31.03.2018 | KRN | 43190.425 | 43190.5312 | 2:33 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK 15-GEETA COLONY. | 773 | PREVENTIVE MAINTENANCE CARRIED OUT
7 | 31.03.2018 | KRN | 43190.4993 | 43190.6243 | 3:00 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | GANDHI NAGAR-KAILASH NAGAR. | 2495 | PREVENTIVE MAINTENANCE CARRIED OUT
8 | 01.04.2018 | KRN | 43191.0896 | 43191.1354 | 1:06 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY, AREA BACKFEEDED | BLOCK 14-GEETA COLONY. | 664
9 | 31.03.2018 | KWN | 43190.4306 | 43190.5702 | 3:21 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK A-MUSTAFABAD (DAYALPUR). | 780 | PREVENTIVE MAINTENANCE CARRIED OUT
10 | 31.03.2018 | KWN | 43190.5368 | 43190.6126 | 1:49 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS CABLE FAULTY, SAME REPAIRED | BLOCK A8-SADAT PUR,KARAWAL NAGAR. | 175
11 | 31.03.2018 | KWN | 43190.6055 | 43190.6621 | 1:21 | HVDS TRANSFORMER | REPLACEMENTY OF HVDS TRANSFORMER | HVDS TRANSFORMER FAULTY, SAME REPLACED | BLOCK H-SHIV VIHAR. | 1307
12 | 31.03.2018 | KWN | 43190.6181 | 43190.6687 | 1:13 | HVDS CABLE & OTHER SYSTEM | TO ATTEND FAULT IN THE LINE | HVDS LEAD FAULTY SAME REPAIRED | JOHRI ENCLAVE-BHAGIRATHI VIHAR. | 1401
13 | 31.03.2018 | KWN | 43190.6764 | 43190.7212 | 1:05 | HVDS TRANSFORMER | REPLACEMENTY OF HVDS TRANSFORMER | HVDS TRANSFORMER FAULTY, SAME REPLACED | PKT W-BLOCK A,BLOCK U-SHIV VIHAR. | 3001
14 | 31.03.2018 | LNR | 43190.4417 | 43190.6875 | 5:54 | PLANNED SHUTDOWN | PROJECT WORK | NEW LTAB INSTALLED | BLOCK G-PREET VIHAR. | 119 | DAMAGED LTAB REPLACED BY NEW ONE
15 | 31.03.2018 | LNR | 43190.4986 | 43190.5905 | 2:12 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK F-GANGA VIHAR,LAXMI NAGAR. | 172 | PREVENTIVE MAINTENANCE CARRIED OUT
16 | 31.03.2018 | MVR | 43190.6028 | 43190.7049 | 2:27 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY, AREA BACKFEEDED | FISH MKT,GAZIPUR. | 656 | CABLE FAULTY, AREA BACKFEEDED
17 | 31.03.2018 | NNG | 43190.4281 | 43190.4792 | 1:14 | HVDS CABLE & OTHER SYSTEM | TO REPAIR HVDS CABLE | HVDS CABLE FAULTY, SAME REPAIRED | ANUP VIHAR-MANDOLI. | 172
18 | 31.03.2018 | NNG | 43190.4424 | 43190.519 | 1:50 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | BABARPUR WEST-BABAR PUR NNG. | 173
19 | 31.03.2018 | NNG | 43190.4528 | 43190.6798 | 5:27 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | BLOCK A-SEWA DHAM. | 215 | PREVENTIVE MAINTENANCE CARRIED OUT
20 | 31.03.2018 | PHG | 43190.4236 | 43190.5785 | 3:43 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | M.M.ROAD,MOTIA KHAN. | 617 | PREVENTIVE MAINTENANCE CARRIED OUT
21 | 31.03.2018 | PHG | 43190.6151 | 43190.6702 | 1:19 | LT SYSTEM FEEDER PILLAR, TERMINATION, ETC. | WIRES DAMAGED DUE TO FIRE ON POLE | DAMAGED WIRE'S REPAIRED | SADAR BAZAR - RAM NAGAR. | 395
22 | 31.03.2018 | PNR | 43190.4688 | 43190.567 | 2:21 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | RAJENDRA BHAWAN-RAJENDRA PLACE. | 130 | PREVENTIVE MAINTENANCE CARRIED OUT
23 | 31.03.2018 | PNR | 43190.4764 | 43190.5507 | 1:47 | HT SYSTEM FAULT | TO ATTEND FAULT IN THE LINE | JUMPER FOUND BROKEN, SAME REPAIRED | KHALSA NAGAR-DEV NAGAR. | 2853
24 | 31.03.2018 | SRD | 43190.4431 | 43190.5614 | 2:50 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | RAMA ICE FECTORY,PRASAD NAGAR. | 656 | PREVENTIVE MAINTENANCE CARRIED OUT
25 | 31.03.2018 | YVR | 43190.4441 | 43190.5217 | 1:52 | DISTRIBUTION TR. | TRANSFORMER MAINTENANCE WORK | TRANSFORMER MAINTENANCE CARRIED OUT | BLOCK F-ZERO PUSTA. | 1584
26 | 31.03.2018 | YVR | 43190.4458 | 43190.5747 | 3:06 | PLANNED SHUTDOWN | PREVENTIVE MAINTENANCE WORK | PREVENTIVE MAINTENANCE CARRIED OUT | YAMUNA VIHAR YAMUNA FLOOD PLAINS. | 44 | PREVENTIVE MAINTENANCE CARRIED OUT
27 | 31.03.2018 | YVR | 43190.5307 | 43190.6047 | 1:47 | HT SYSTEM FAULT | TRIPPING | CABLE FAULTY, AREA BACKFEEDED | MAHILA COLONY-SEELAMPUR,JAFFRABAD-MAUJ PUR. | 785